## CALCULATOR
Panduit Patch Cord Approximate Diameters
[7 empty] | Cat. | AWG | in. |  | mm
[7 empty] | 5e | 24 | 0.215 |  | 5.461
[7 empty] | 6 | 28 | 0.15 |  | 3.81
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.25 | 1 |  |  |  |  | 6A | 24 | 0.275 |  | 6.985
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
PR2V PatchRunner™ 2 Vertical Cable Managers | PR2VD06 | 6" wide | 45.11 | 27.26 | 72.37 | 275 | 166 | 442 |  | 459 | 277 | 737
| PR2VFD06 | 6" wide, front only | 45.11 | 0 | 45.11 | 275 | 0 | 275 |  | 459 | 0 | 459
| PR2VD08 | 8" wide | 63.71 | 39.73 | 103.44 | 389 | 242 | 632 |  | 648 | 404 | 1053
| PR2VFD08 | 8" wide, front only | 63.71 | 0 | 63.71 | 389 | 0 | 389 |  | 648 | 0 | 648
| PR2VD10 | 10" wide | 82.31 | 52.21 | 134.52 | 503 | 319 | 822 |  | 838 | 531 | 1370
| PR2VFD10 | 10" wide, front only | 82.31 | 0 | 82.31 | 503 | 0 | 503 |  | 838 | 0 | 838
| PR2VD12 | 12" wide | 100.9 | 64.68 | 165.58 | 616 | 395 | 1011 |  | 1027 | 658 | 1686
| PR2VFD12 | 12" wide, front only | 100.9 | 0 | 100.9 | 616 | 0 | 616 |  | 1027 | 0 | 1027
| Single PR2V Finger |  |  |  | 5.8 | 35 |  |  |  | 59
PRV PatchRunner™ Vertical Cable Managers | PRV6 | 6" wide | 38.5 | 26.6 | 65.1 | 235 | 162 | 397 |  | 392 | 270 | 663
| PRVF6 | 6" wide, front only | 38.5 | 0 | 38.5 | 235 | 0 | 235 |  | 392 | 0 | 392
| PRV8 | 8" wide | 55.3 | 37.7 | 93 | 337 | 230 | 568 |  | 563 | 384 | 947
| PRVF8 | 8" wide, front only | 55.3 | 0 | 55.3 | 337 | 0 | 337 |  | 563 | 0 | 563
| PRV10 | 10" wide | 72 | 48.8 | 120.8 | 440 | 298 | 738 |  | 733 | 497 | 1230
| PRVF10 | 10" wide, front only | 72 | 0 | 72 | 440 | 0 | 440 |  | 733 | 0 | 733
| PRV12 | 12" wide | 88.8 | 59.9 | 148.7 | 542 | 366 | 908 |  | 904 | 610 | 1514
| PRVF12 | 12" wide, front only | 88.8 | 0 | 88.8 | 542 | 0 | 542 |  | 904 | 0 | 904
| PRV15 | 15" wide | 113.9 | 76.5 | 190.4 | 696 | 467 | 1163 |  | 1160 | 779 | 1939
| PRVF15 | 15" wide, front only | 113.9 | 0 | 113.9 | 696 | 0 | 696 |  | 1160 | 0 | 1160
| Single PRV Finger |  |  |  | 4.7 | 28 |  |  |  | 47
Note: Door brackets and cable slack spools reduce cable capacity.
PE2V PatchRunner™ 2 High Capacity Vertical Cable Managers | PE2VD06 | 6" wide | 66.1018 | 44.2782 | 110.38 | 403 | 270 | 674 |  | 673 | 451 | 1124
| PE2VFD06 | 6" wide, front only | 66.1018 | 0 | 66.1018 | 403 | 0 | 403 |  | 673 | 0 | 673
| PE2VD08 | 8" wide | 92.4809 | 63.0973 | 155.5782 | 565 | 385 | 950 |  | 942 | 642 | 1584
| PE2VFD08 | 8" wide, front only | 92.4809 | 0 | 92.4809 | 565 | 0 | 565 |  | 942 | 0 | 942
| PE2VD10 | 10" wide | 118.8599 | 81.9639 | 200.8238 | 726 | 500 | 1227 |  | 1210 | 834 | 2045
| PE2VFD10 | 10" wide, front only | 118.8599 | 0 | 118.8599 | 726 | 0 | 726 |  | 1210 | 0 | 1210
| PE2VD12 | 12" wide | 145.239 | 100.7355 | 245.9745 | 887 | 615 | 1503 |  | 1479 | 1026 | 2505
| PE2VFD12 | 12" wide, front only | 145.239 | 0 | 145.239 | 887 | 0 | 887 |  | 1479 | 0 | 1479
| Single PE2V Finger |  |  |  | 5.8 | 35 |  |  |  | 59
PEV PatchRunner™ High Capacity Vertical Cable Managers | PEV6 | 6" wide | 67.1 | 45.9 | 113 | 410 | 280 | 690 |  | 683 | 467 | 1151
| PEVF6 | 6" wide, front only | 67.1 | 0 | 67.1 | 410 | 0 | 410 |  | 683 | 0 | 683
| PEV8 | 8" wide | 92.8 | 64.3 | 157.1 | 567 | 392 | 960 |  | 945 | 654 | 1600
| PEVF8 | 8" wide, front only | 92.8 | 0 | 92.8 | 567 | 0 | 567 |  | 945 | 0 | 945
| PEV10 | 10" wide | 118.6 | 82.6 | 201.2 | 724 | 504 | 1229 |  | 1208 | 841 | 2049
| PEVF10 | 10" wide, front only | 118.6 | 0 | 118.6 | 724 | 0 | 724 |  | 1208 | 0 | 1208
| PEV12 | 12" wide | 144.4 | 101 | 245.4 | 882 | 617 | 1499 |  | 1470 | 1028 | 2499
| PEVF12 | 12" wide, front only | 144.4 | 0 | 144.4 | 882 | 0 | 882 |  | 1470 | 0 | 1470
| Single PEV Finger |  |  |  | 5.7 | 34 |  |  |  | 58
Note: Door brackets and cable slack spools reduce cable capacity.
WMPV NetRunner™ Vertical Cable Managers | WMPV22E | 4.9" wide, 22RU | 17.3 | 17.3 | 34.6 | 105 | 105 | 211 |  | 176 | 176 | 352
| WMPVF22E | 4.9" wide, 22RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| WMPV45E | 4.9" wide, 45RU | 17.3 | 17.3 | 34.6 | 105 | 105 | 211 |  | 176 | 176 | 352
| WMPVF45E | 4.9" wide, 45RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| WMPVHC45E | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 187 | 187 | 375 |  | 312 | 312 | 625
| WMPVHCF45E | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 187 | 0 | 187 |  | 312 | 0 | 312
| Single WMPV Finger |  |  |  | 3.7 | 22 |  |  |  | 37
| Single WMPVHC Finger |  |  |  | 4.7 | 28 |  |  |  | 47
NRV NetRunner™ High Capacity Vertical Cable Managers | NRV6 | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 187 | 187 | 375 |  | 312 | 312 | 625
| NRVF6 | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 187 | 0 | 187 |  | 312 | 0 | 312
| NRV10 | 10" wide, 45RU | 49.1 | 49.1 | 98.2 | 300 | 300 | 600 |  | 500 | 500 | 1000
| NRVF10 | 10" wide, 45RU, front only | 49.1 | 0 | 49.1 | 300 | 0 | 300 |  | 500 | 0 | 500
| NRV12 | 12" wide, 45RU | 60.7 | 60.7 | 121.4 | 370 | 370 | 741 |  | 618 | 618 | 1236
| NRVF12 | 12" wide, 45RU, front only | 60.7 | 0 | 60.7 | 370 | 0 | 370 |  | 618 | 0 | 618
| Single NRV Finger |  |  |  | 4.7 | 28 |  |  |  | 47
WMP PatchLink™ Horizontal Cable Managers | WMP1E | 2RU, front/rear | 7.6 | 10.6 | 18.2 | 46 | 64 | 111 |  | 77 | 107 | 185
| WMPF1E | 2RU, front only | 7.6 | 0 | 7.6 | 46 | 0 | 46 |  | 77 | 0 | 77
| WMPH2E | 2RU, front/rear, w/ bend rad. clips | 5.9 | 10.6 | 16.5 | 36 | 64 | 100 |  | 60 | 107 | 168
| WMPHF2E | 2RU, front only, w/ bend rad. clips | 5.9 | 0 | 5.9 | 36 | 0 | 36 |  | 60 | 0 | 60
| WMPSE | 1RU, front/rear | 3.5 | 6.3 | 9.8 | 21 | 38 | 59 |  | 35 | 64 | 99
| WMPFSE | 1RU, front only | 3.5 | 0 | 3.5 | 21 | 0 | 21 |  | 35 | 0 | 35
| WMPLSE | 1RU, front/rear, short depth | 2.1 | 6.3 | 8.4 | 12 | 38 | 51 |  | 21 | 64 | 85
| WMPLFSE | 1RU, front only, short depth | 2.1 | 0 | 2.1 | 12 | 0 | 12 |  | 21 | 0 | 21
Note: Rear section may be partially blocked by rack posts
NCMH NetManager™ Horizontal Cable Managers | NCMH2 | 2RU, front/rear | 6 | 8 | 14 | 36 | 48 | 85 |  | 61 | 81 | 142
| NCMHF2 | 2RU, front only | 6 | 0 | 6 | 36 | 0 | 36 |  | 61 | 0 | 61
| NCMHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 14 | 0 | 14 |  | 23 | 0 | 23
NM NetManager™ High Capacity Horizontal Cable Managers | NM1 | 1RU, front/rear | 3.3 | 4.1 | 7.4 | 20 | 25 | 45 |  | 33 | 41 | 75
| NMF1 | 1RU, front only | 3.3 | 0 | 3.3 | 20 | 0 | 20 |  | 33 | 0 | 33
| NM2 | 2RU, front/rear | 9.8 | 11.1 | 20.9 | 59 | 67 | 127 |  | 99 | 113 | 212
| NMF2 | 2RU, front only | 9.8 | 0 | 9.8 | 59 | 0 | 59 |  | 99 | 0 | 99
| NM3 | 3RU, front/rear | 17.3 | 22 | 39.3 | 105 | 134 | 240 |  | 176 | 224 | 400
| NMF3 | 3RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| NM4 | 4RU, front/rear | 24.3 | 31.9 | 56.2 | 148 | 194 | 343 |  | 247 | 324 | 572
| NMF4 | 4RU, front only | 24.3 | 0 | 24.3 | 148 | 0 | 148 |  | 247 | 0 | 247
Note: Rear section may be partially blocked by rack posts
CMPH Open-Access™ Horizontal Cable Managers | CMPH1 | 1RU, front/rear | 2.3 | 2.9 | 5.2 | 14 | 17 | 31 |  | 23 | 29 | 52
| CMPHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 14 | 0 | 14 |  | 23 | 0 | 23
| CMPH2 | 2RU, front/rear | 5.3 | 10.8 | 16.1 | 32 | 66 | 98 |  | 53 | 110 | 163
| CMPHF2 | 2RU, front only | 5.3 | 0 | 5.3 | 32 | 0 | 32 |  | 53 | 0 | 53
| CMPHH2 | 2RU, front only, larger D-rings | 10.8 | 0 | 10.8 | 66 | 0 | 66 |  | 110 | 0 | 110
| CMPHHF1 | 1RU, front only, larger D-rings | 2.9 | 0 | 2.9 | 17 | 0 | 17 |  | 29 | 0 | 29
Note: Rear section may be partially blocked by rack posts
PEHF PatchRunner™ High Capacity Horizontal Cable Managers | PEHF2 | 2RU, front only | 16.6 | 0 | 16.6 | 101 | 0 | 101 |  | 169 | 0 | 169
| PEHF3 | 3RU, front only | 29.6 | 0 | 29.6 | 180 | 0 | 180 |  | 301 | 0 | 301
| PEHF4 | 4RU, front only | 42.8 | 0 | 42.8 | 261 | 0 | 261 |  | 435 | 0 | 435
CMVDR Vertical D-rings | CMVDR1 | 5.70"L x 2.00"W |  |  | 6 |  |  | 36 |  |  |  | 61
| CMVDR1S | 3.30"L x 2.00"W |  |  | 3 |  |  | 18 |  |  |  | 30
| CMVDR2 | 5.70"L x 3.00"W |  |  | 10.8 |  |  | 66 |  |  |  | 110
| CMVDR2S | 3.30"L x 3.00"W |  |  | 6 |  |  | 36 |  |  |  | 61
| CMVDRC | between-racks, 5.60"L x 8.00"W |  |  | 24 |  |  | 146 |  |  |  | 244
CM Cable Routing Troughs | CMLT19 | lower trough w/ bend radius |  |  | 22.7 |  |  | 138 |  |  |  | 231
| CMUT19 | upper trough w/ bend radius |  |  | 8.2 |  |  | 50 |  |  |  | 83
| CMT4 | horizontal trough |  |  | 21.9 |  |  | 133 |  |  |  | 223
*Capacity is calculated for within the trough channel only. Higher capacities can be achieved when cables are tied together.
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2418 | side mount, 2"W x 4"D x 2.6'H | 5.7 | 0 | 5.7 | 34 | 0 | 34 |  | 58 | 0 | 58
| CWMPV3418 | side mount, 3"W x 4"D x 2.6'H | 9.1 | 0 | 9.1 | 55 | 0 | 55 |  | 92 | 0 | 92
| CWMPV2440 | side mount, 2"W x 4"D x 6'H | 5.7 | 0 | 5.7 | 34 | 0 | 34 |  | 58 | 0 | 58
| CWMPV3440 | side mount, 3"W x 4"D x 6'H | 9.1 | 0 | 9.1 | 55 | 0 | 55 |  | 92 | 0 | 92
| CWMPV2318 | side mount, 2"W x 3"D x 2.6'H | 5.2 | 0 | 5.2 | 31 | 0 | 31 |  | 52 | 0 | 52
| CWMPV3318 | side mount, 3"W x 3"D x 2.6'H | 7.8 | 0 | 7.8 | 47 | 0 | 47 |  | 79 | 0 | 79
| CWMPV2340 | side mount, 2"W x 3"D x 6'H | 5.2 | 0 | 5.2 | 31 | 0 | 31 |  | 52 | 0 | 52
| CWMPV3340 | side mount, 3"W x 3"D x 6'H | 7.8 | 0 | 7.8 | 47 | 0 | 47 |  | 79 | 0 | 79
J-PRO & J-MOD J Hooks | JP75^ | J-Pro™ cable support, 0.75" |  |  | 0.626 |  |  | 6 |  |  |  | 8
| JP131^ | J-Pro™ cable support, 1.31" |  |  | 1.74 |  |  | 17 |  |  |  | 24
| JP2^ | J-Pro™ cable support, 2.0" |  |  | 3.155 |  |  | 32 |  |  |  | 44
| JP4^ | J-Pro™ cable support, 4.0" |  |  | 13.478 |  |  | 137 |  |  |  | 192
| JMJH2^ | J-Mod™ cable support, 2.0" |  |  | 3.037 |  |  | 30 |  |  |  | 43
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
Cable Capacity Calculator V4

## numbers (hidden)
in. | no
mm | yes
30% | 50%
50% | 70%
0.215 | 0.185 | 0.275 | 0.15 | 0.235