## Content
Content
Modbus communication table h3+
Reference | : | 6LE005605A
Version | : | a, september 2018
Identification
MCCB and Communication module identification information
Measures
All availables measurements
Indicators
Status and maintenance indicators
History
Custom Alarms and trip alarms logged events
Protection settings change logged events
Configuration
Meassurements Settings
Alarm settings
Protection settings
Communication
Modbus and MCCB Communication registers
Registers for I/O communication module HTC320H
Write commands registers
Note
All registers described in Configuration are Read and Write access data, except "Instantaneous protection status" and "Data writing autorisation status".
Specifics secured commands have been implemented to realise a write access procedure.
Please contact us for more details.
For more details on Custom alarm ID, Alarm ID and Assignment ID mentioned in History and Configuration, please contact us.

## Identification
Device Identification
Product reference | [5 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Address DEC | Address HEX | Lengh (word) | Data Type | Function | Further information
Communication Module Vendor Name | 4096 | 1000 | 16 | STRING | H'03' | "Hager" : Hex 48 61 67 65 72
Communication Module Product code | 4112 | 1010 | 16 | STRING | H'03' | Example: "HTC310H": Hex 48 54 43 33 31 30 48
Communication Module SW version | 4128 | 1020 | 2 | U32 | H'03' | Example: v1.2.2 : Hex 01 02 02 00
Communication Module Vendor URL | 4130 | 1022 | 16 | STRING | H'03' | "http://www.hager.com"
Communication Module Product name | 4146 | 1032 | 16 | STRING | H'03' | "H3+ Modbus Interface"
Communication Module Model name | 4162 | 1042 | 16 | STRING | H'03' | Example: "Module without IO"
Communication Module User application name | 4178 | 1052 | 16 | STRING | H'03' | "APL"
Communication Module Hardware version | 4194 | 1062 | 2 | U32 | H'03' | Example: Hex 01 03 00 00
Communication Module Serial number | 4196 | 1064 | 16 | STRING | H'03' | Example: "17270910015HTC310HA"
Communication Module Site code | 4212 | 1074 | 2 | U32 | H'03' | Example: Dec 4294967295
Communication Module Production Day | 4214 | 1076 | 1 | U16 | H'03' | 225
Communication Module Production Year | 4215 | 1077 | 1 | U16 | H'03' | 2018
MCCB Production site | 4240 | 1090 | 1 | STRING | H'03' | Example: France: Hex 00 46
MCCB Serial Number | 4241 | 1091 | 2 | U32 | H'03' | Example: Hex 00 00 00 01
MCCB Production day | 4243 | 1093 | 1 | U16 | H'03' | Example: Hex 01 59
MCCB Production year | 4244 | 1094 | 1 | U16 | H'03' | Example: Hex 00 01
MCCB Hardware version | 4245 | 1095 | 2 | U32 | H'03' | Example: Hex 00 03 00 00
MCCB Software version | 4247 | 1097 | 2 | U32 | H'03' | Example: Hex 00 09 00 00
MCCB Communication version | 4249 | 1099 | 2 | U32 | H'03' | Example: Hex 01 01 00 00
MCCB Brand name | 4251 | 109B | 1 | U16 | H'03' | Hager: Hex 00 00
MCCB Range name | 4252 | 109C | 1 | U16 | H'03' | h3+: Hex 00 00
MCCB Frame size | 4253 | 109D | 1 | U16 | H'03' | 0: P160 1: P250 2: P250Hbc 3: P630 Example: P160: Hex 00 00
MCCB Nominal rating | 4254 | 109E | 1 | U16 | H'03' | 40, 100, 125, 160, 200, 250, 400, 630A Example: 40A: Hex 00 28
MCCB Number of pole | 4255 | 109F | 1 | U16 | H'03' | Example: 4 poles: 00 04
MCCB Trip unit type | 4256 | 10A0 | 1 | U16 | H'03' | 0: LSnI 1: LSI 2: LSIG 3: Energy Example: Energy: Hex 00 03

## Measures
Measures
Product reference | [7 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information
Phase to phase voltage U12 | V | 0.001 | 4352 | 1100 | 2 | U32 | H'03' | Example: 405.300V: Hex 00 06 2F 34
Phase to phase voltage U23 | V | 0.001 | 4354 | 1102 | 2 | U32 | H'03' | Example: 404.500V: Hex 00 06 2C 14
Phase to phase voltage U31 | V | 0.001 | 4356 | 1104 | 2 | U32 | H'03' | Example: 405.300V: Hex 00 06 2F 34
Phase to neutral volatge V1N | V | 0.001 | 4358 | 1106 | 2 | U32 | H'03' | Example: 233.100V: Hex 00 03 8E 8C
Phase to neutral voltage V2N | V | 0.001 | 4360 | 1108 | 2 | U32 | H'03' | Example: 234.900V: Hex 00 03 95 94
Phase to neutral voltage V3N | V | 0.001 | 4362 | 110A | 2 | U32 | H'03' | Example: 232.800V: Hex 00 03 8D 60
Maximum phase to phase voltage between U12 / U23 / U31 | V | 0.001 | 4364 | 110C | 2 | U32 | H'03' | Example: 405.500V: Hex 00 06 2F FC
Minimum phase to phase voltage between U12 / U23 / U31 | V | 0.001 | 4366 | 110E | 2 | U32 | H'03' | Example: 403.800V: Hex 00 06 29 58
Maximum phase to neutral voltage between V1N / V2N / V3N | V | 0.001 | 4368 | 1110 | 2 | U32 | H'03' | Example: 235.100V: Hex 00 03 96 5C
Minimum phase to neutral voltage between V1N / V2N / V3N | V | 0.001 | 4370 | 1112 | 2 | U32 | H'03' | Example: 232.600V: Hex 00 03 8C 98
Arithmetic average of U12, U23 & U31 : (U12+U23+U31) / 3 = Umoy L-L. | V | 0.001 | 4372 | 1114 | 2 | U32 | H'03' | Example: 404.900V: Hex 00 06 2D A4
Arithmetic average of V1N, V2N & V3N : (V1N+V2N+V3N) / 3 = Vmoy L-N | V | 0.001 | 4374 | 1116 | 2 | U32 | H'03' | Example: 234.000V: Hex 00 03 92 10
Unbalanced U12 vs Umoy L-L | % | 0.1 | 4376 | 1118 | 2 | S32 | H'03' | Example: 0.1%: Hex 00 00 00 01
Unbalanced U23 vs Umoy L-L | % | 0.1 | 4378 | 111A | 2 | S32 | H'03' | Example: 0.2%: Hex 00 00 00 02
Unbalanced U31 vs Umoy L-L | % | 0.1 | 4380 | 111C | 2 | S32 | H'03' | Example: -0.1%: Hex FF FF FF FF
Maximum unbalanced composite voltage | % | 0.1 | 4382 | 111E | 2 | S32 | H'03' | Example: 0.1%: Hex 00 00 00 01
Unbalanced V1N vs Vmoy L-N | % | 0.1 | 4384 | 1120 | 2 | S32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Unbalanced V2N vs Vmoy L-N | % | 0.1 | 4386 | 1122 | 2 | S32 | H'03' | Example: 0.5%: Hex 00 00 00 05
Unbalanced V3N vs Vmoy L-N | % | 0.1 | 4388 | 1124 | 2 | S32 | H'03' | Example: -0.3%: Hex FF FF FF FD
Maximum unbalanced simple voltage | % | 0.1 | 4390 | 1126 | 2 | S32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Current on phase 1: I1 | A | 0.001 | 4392 | 1128 | 2 | U32 | H'03' | Example: 15.000A: Hex 00 00 3A 98
Current on phase 2: I2 | A | 0.001 | 4394 | 112A | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Current on phase 3: I3 | A | 0.001 | 4396 | 112C | 2 | U32 | H'03' | Example: 14.400A: Hex 00 00 38 40
Current on neutral: IN | A | 0.001 | 4398 | 112E | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Ground fault current IG | A | 0.001 | 4400 | 1130 | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Maximum current between I1, I2, I3 and IN | A | 0.001 | 4402 | 1132 | 2 | U32 | H'03' | Example: 14.200A: Hex 00 00 37 78
Minimum current between I1, I2, I3 | A | 0.001 | 4404 | 1134 | 2 | U32 | H'03' | Example: 13.800A: Hex 00 00 35 E8
Arithmetic average of I1, I2 & I3 : (I1+I2+I3) / 3 = Imoy | A | 0.001 | 4406 | 1136 | 2 | U32 | H'03' | Example: 13.900A: Hex 00 00 36 4C
Unbalanced I1 vs Imoy | % | 0.1 | 4408 | 1138 | 2 | S32 | H'03' | Example: 4.9%: Hex 00 00 00 31
Unbalanced I2 vs Imoy | % | 0.1 | 4410 | 113A | 2 | S32 | H'03' | Example: -3.7%: Hex FF FF FF DB
Unbalanced I3 vs Imoy | % | 0.1 | 4412 | 113C | 2 | S32 | H'03' | Example: -2.1%: Hex FF FF FF EB
Unbalanced IN vs Imoy | % | 0.1 | 4414 | 113E | 2 | S32 | H'03' | Example: -100.0%: Hex FF FF FC 18
Maximum unbalanced current | % | 0.1 | 4416 | 1140 | 2 | S32 | H'03' | Example: -100.0%: Hex FF FF FC 18
Active power on phase 1 P1 | W | 1 | 4418 | 1142 | 2 | S32 | H'03' | Example: 2200W: Hex 00 00 08 98
Active power on phase 2 P2 | W | 1 | 4420 | 1144 | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
Active power on phase 3 P3 | W | 1 | 4422 | 1146 | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
Total active power Ptot | W | 1 | 4424 | 1148 | 2 | S32 | H'03' | Example: 5900W: Hex 00 00 17 0C
Reactive power on phase 1 Q1 | var | 1 | 4426 | 114A | 2 | S32 | H'03' | Example: 2900var: Hex 00 00 0B 54
Reactive power on phase 2 Q2 | var | 1 | 4428 | 114C | 2 | S32 | H'03' | Example: 2900var: Hex 00 00 0B 54
Reactive power on phase 3 Q3 | var | 1 | 4430 | 114E | 2 | S32 | H'03' | Example: 2800var: Hex 00 00 0A F0
Total reactive power Qtot | var | 1 | 4432 | 1150 | 2 | S32 | H'03' | Example: 8700var: Hex 00 00 21 FC
Apparent power on phase 1 S1 | VA | 1 | 4434 | 1152 | 2 | U32 | H'03' | Example: 3900VA: Hex 00 00 0F 3C
Apparent power on phase 2 S2 | VA | 1 | 4436 | 1154 | 2 | U32 | H'03' | Example: 3200VA: Hex 00 00 0C 80
Apparent power on phase 3 S3 | VA | 1 | 4438 | 1156 | 2 | U32 | H'03' | Example: 3200VA: Hex 00 00 0C 80
Total apparent power Stot | VA | 1 | 4440 | 1158 | 2 | U32 | H'03' | Example: 10100VA: Hex 00 00 27 74
Power factor on phase 1 PF1 | - | 0.0001 | 4442 | 115A | 2 | S32 | H'03' | Example: 0.5500: Hex 00 00 15 7C
Power factor on phase 2 PF2 | - | 0.0001 | 4444 | 115C | 2 | S32 | H'03' | Example: 0.5500: Hex 00 00 15 7C
Power factor on phase 3 PF3 | - | 0.0001 | 4446 | 115E | 2 | S32 | H'03' | Example: 0.4100: Hex 00 00 10 04
Total power factor PFtot | - | 0.0001 | 4448 | 1160 | 2 | S32 | H'03' | Example: 0.5300: Hex 00 00 14 B4
Fundamental power factor on phase 1 cosϕ1 | - | 0.0001 | 4450 | 1162 | 2 | S32 | H'03' | Example: 0.6500: Hex 00 00 19 64
Fundamental power factor on phase 2 cosϕ2 | - | 0.0001 | 4452 | 1164 | 2 | S32 | H'03' | Example: 0.4600: Hex 00 00 11 F8
Fundamental power factor on phase 3 cosϕ3 | - | 0.0001 | 4454 | 1166 | 2 | S32 | H'03' | Example: 0.4800: Hex 00 00 12 C0
Total fundamental power factor cosϕtot | - | 0.0001 | 4456 | 1168 | 2 | S32 | H'03' | Example: 0.5100: Hex 00 00 13 EC
Network frequency F | Hz | 0.001 | 4458 | 116A | 2 | U32 | H'03' | Example: 49.990Hz: Hex 00 00 C3 46
THD of U12 | % | 0.1 | 4460 | 116C | 2 | U32 | H'03' | Example: 0.8%: Hex 00 00 00 08
THD of U23 | % | 0.1 | 4462 | 116E | 2 | U32 | H'03' | Example: 0.8%: Hex 00 00 00 08
THD of U31 | % | 0.1 | 4464 | 1170 | 2 | U32 | H'03' | Example: 0.9%: Hex 00 00 00 09
THD of V1N | % | 0.1 | 4466 | 1172 | 2 | U32 | H'03' | Example: 1.2%: Hex 00 00 00 0C
THD of V2N | % | 0.1 | 4468 | 1174 | 2 | U32 | H'03' | Example: 1.1%: Hex 00 00 00 0B
THD of V3N | % | 0.1 | 4470 | 1176 | 2 | U32 | H'03' | Example: 1.2%: Hex 00 00 00 0C
THD of I1 | % | 0.1 | 4472 | 1178 | 2 | U32 | H'03' | Example: 4.7%: Hex 00 00 00 2F
THD of I2 | % | 0.1 | 4474 | 117A | 2 | U32 | H'03' | Example: 4.2%: Hex 00 00 00 2A
THD of I3 | % | 0.1 | 4476 | 117C | 2 | U32 | H'03' | Example: 6.6%: Hex 00 00 00 42
Maximun THD between I1, I2 & I3 | % | 0.1 | 4478 | 117E | 2 | U32 | H'03' | Example: 6.8%: Hex 00 00 00 44
Minimum Phase to phase voltage U12 | V | 0.001 | 4480 | 1180 | 2 | U32 | H'03' | Example: 317.900V: Hex 00 04 D9 CC
Minimum U12 Timestamp machine | s | 1 | 4482 | 1182 | 2 | U32 | H'03' | Example: 26153940s: Hex 01 8F 13 D4
Minimum U12 Timestamp user | s | 1 | 4484 | 1184 | 2 | U32 | H'03' | Example: 14109798s: Hex 00 D7 4C 66
Minimum Phase to phase voltage U23 | V | 0.001 | 4486 | 1186 | 2 | U32 | H'03' | Example: 321.400V: Hex 00 04 E7 78
Minimum U23 Timestamp machine | s | 1 | 4488 | 1188 | 2 | U32 | H'03' | Example: 26153940s: Hex 01 8F 13 D4
Minimum U23 Timestamp user | s | 1 | 4490 | 118A | 2 | U32 | H'03' | Example: 14109798s: Hex 00 D7 4C 66
Minimum Phase to phase voltage U31 | V | 0.001 | 4492 | 118C | 2 | U32 | H'03' | Example: 320.100V: Hex 00 04 E2 64
Minimum U31 Timestamp machine | s | 1 | 4494 | 118E | 2 | U32 | H'03' | Example: 26153940s: Hex 01 8F 13 D4
Minimum U31 Timestamp user | s | 1 | 4496 | 1190 | 2 | U32 | H'03' | Example: 14109798s: Hex 00 D7 4C 66
Minimum Phase to neutral voltage V1N | V | 0.001 | 4498 | 1192 | 2 | U32 | H'03' | Example: 183.400V: Hex 00 02 CC 68
Minimum V1N Timestamp machine | s | 1 | 4500 | 1194 | 2 | U32 | H'03' | Example: 26153940s: Hex 01 8F 13 D4
Minimum V1N Timestamp user | s | 1 | 4502 | 1196 | 2 | U32 | H'03' | Example: 14109798s: Hex 00 D7 4C 66
Minimum Phase to neutral voltage V2N | V | 0.001 | 4504 | 1198 | 2 | U32 | H'03' | Example: 185.000V: Hex 00 02 D2 A8
Minimum V2N Timestamp machine | s | 1 | 4506 | 119A | 2 | U32 | H'03' | Example: 26153940s: Hex 01 8F 13 D4
Minimum V2N Timestamp user | s | 1 | 4508 | 119C | 2 | U32 | H'03' | Example: 14109798s: Hex 00 D7 4C 66
Minimum Phase to neutral voltage V3N | V | 0.001 | 4510 | 119E | 2 | U32 | H'03' | Example: 178.900V: Hex 00 02 BA D4
Minimum V3N Timestamp machine | s | 1 | 4512 | 11A0 | 2 | U32 | H'03' | Example: 25970412s: Hex 01 8C 46 EC
Minimum V3N Timestamp user | s | 1 | 4514 | 11A2 | 2 | U32 | H'03' | Example: 13926270s: Hex 00 D4 7F 7E
Minimum Arithmetic average of U12, U23 & U31 : (U12+U23+U31) / 3 = Umoy L-L. | V | 0.001 | 4516 | 11A4 | 2 | U32 | H'03' | Example: 319.800V: Hex 00 04 E1 38
Minimum Arithmetic average of V1N, V2N & V3N : (V1N+V2N+V3N) / 3 = Vmoy L-N | V | 0.001 | 4518 | 11A6 | 2 | U32 | H'03' | Example: 184.600V: Hex 00 02 D1 18
Minimum Unbalanced U12 vs Umoy L-L | % | 0.1 | 4520 | 11A8 | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum Unbalanced U23 vs Umoy L-L | % | 0.1 | 4522 | 11AA | 2 | S32 | H'03' | Example: 2.0%: Hex 00 00 00 14
Minimum Unbalanced U31 vs Umoy L-L | % | 0.1 | 4524 | 11AC | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum of maximum unbalanced composite voltage | % | 0.1 | 4526 | 11AE | 2 | S32 | H'03' | Example: 3.0%: Hex 00 00 00 1E
Minimum Unbalanced V1N vs Vmoy L-N | % | 0.1 | 4528 | 11B0 | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum Unbalanced V2N vs Vmoy L-N | % | 0.1 | 4530 | 11B2 | 2 | S32 | H'03' | Example: 2.0%: Hex 00 00 00 14
Minimum Unbalanced V3N vs Vmoy L-N | % | 0.1 | 4532 | 11B4 | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum of Maximum unbalanced simple voltage | % | 0.1 | 4534 | 11B6 | 2 | S32 | H'03' | Example: 3.0%: Hex 00 00 00 1E
Minimum current on phase 1: I1 | A | 0.001 | 4536 | 11B8 | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Minimum current on phase 2: I2 | A | 0.001 | 4538 | 11BA | 2 | U32 | H'03' | Example: 14.200A: Hex 00 00 37 78
Minimum current on phase 3: I3 | A | 0.001 | 4540 | 11BC | 2 | U32 | H'03' | Example: 13.800A: Hex 00 00 35 E8
Minimum current on neutral: IN | A | 0.001 | 4542 | 11BE | 2 | U32 | H'03' | Example: 13.900A: Hex 00 00 36 4C
Minimum value of the calculated current Ig | A | 0.001 | 4544 | 11C0 | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Maximum of Minimum. of I1, I2, I3 and IN | A | 0.001 | 4546 | 11C2 | 2 | U32 | H'03' | Example: 14.200A: Hex 00 00 37 78
Minimum of I1, I2 and I3 | A | 0.001 | 4548 | 11C4 | 2 | U32 | H'03' | Example: 13.800A: Hex 00 00 35 E8
Arithmetic average of Minimum. of I1, I2 & I3 : (I1+I2+I3) / 3 = Imoy | A | 0.001 | 4550 | 11C6 | 2 | U32 | H'03' | Example: 13.900A: Hex 00 00 36 4C
Minimum unbalanced I1 vs Imoy | % | 0.1 | 4552 | 11C8 | 2 | S32 | H'03' | Example: 2.0%: Hex 00 00 00 14
Minimum unbalanced I2 vs Imoy | % | 0.1 | 4554 | 11CA | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum unbalanced I3 vs Imoy | % | 0.1 | 4556 | 11CC | 2 | S32 | H'03' | Example: 3.0%: Hex 00 00 00 1E
Minimum unbalanced IN vs Imoy | % | 0.1 | 4558 | 11CE | 2 | S32 | H'03' | Example: 1.0%: Hex 00 00 00 0A
Minimum of Max unbalanced current | % | 0.1 | 4560 | 11D0 | 2 | S32 | H'03' | Example: 3.0%: Hex 00 00 00 1E
Minimum Active power on phase 1 P1 | W | 1 | 4562 | 11D2 | 2 | S32 | H'03' | Example: 2200W: Hex 00 00 08 98
Minimum Active power on phase 2 P2 | W | 1 | 4564 | 11D4 | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
Minimum Active power on phase 3 P3 | W | 1 | 4566 | 11D6 | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
Minimum Total active power Ptot | W | 1 | 4568 | 11D8 | 2 | S32 | H'03' | Example: 5900W: Hex 00 00 17 0C
Minimum Reactive power on phase 1 Q1 | var | 1 | 4570 | 11DA | 2 | S32 | H'03' | Example: 2900var: Hex 00 00 0B 54
Minimum Reactive power on phase 2 Q2 | var | 1 | 4572 | 11DC | 2 | S32 | H'03' | Example: 2900var: Hex 00 00 0B 54
Minimum Reactive power on phase 2 Q2 | var | 1 | 4574 | 11DE | 2 | S32 | H'03' | Example: 2800var: Hex 00 00 0A F0
Minimum Total reactive power Qtot | var | 1 | 4576 | 11E0 | 2 | S32 | H'03' | Example: 8700var: Hex 00 00 21 FC
Minimum Apparent power on phase 1 S1 | VA | 1 | 4578 | 11E2 | 2 | U32 | H'03' | Example: 3900VA: Hex 00 00 0F 3C
Minimum Apparent power on phase 2 S2 | VA | 1 | 4580 | 11E4 | 2 | U32 | H'03' | Example: 3200VA: Hex 00 00 0C 80
Minimum Apparent power on phase 3 S3 | VA | 1 | 4582 | 11E6 | 2 | U32 | H'03' | Example: 3200VA: Hex 00 00 0C 80
Minimum Total apparent power Stot | VA | 1 | 4584 | 11E8 | 2 | U32 | H'03' | Example: 10100VA: Hex 00 00 27 74
Minimum Power factor on phase 1 PF1 | - | 0.0001 | 4586 | 11EA | 2 | S32 | H'03' | Example: 0.0100: Hex 00 00 00 64
Minimum Power factor on phase 2 PF2 | - | 0.0001 | 4588 | 11EC | 2 | S32 | H'03' | Example: 0.0100: Hex 00 00 00 64
Minimum Power factor on phase 3 PF3 | - | 0.0001 | 4590 | 11EE | 2 | S32 | H'03' | Example: 0.2700: Hex 00 00 0A 8C
Minimum Total power factor PFtot | - | 0.0001 | 4592 | 11F0 | 2 | S32 | H'03' | Example: 0.1900: Hex 00 00 07 6C
Minimum Fundamental power factor on phase 1 cosϕ1 | - | 0.0001 | 4594 | 11F2 | 2 | S32 | H'03' | Example: 0.0100: Hex 00 00 00 64
Minimum Fundamental power factor on phase 2 cosϕ2 | - | 0.0001 | 4596 | 11F4 | 2 | S32 | H'03' | Example: 0.0200: Hex 00 00 00 C8
Minimum Fundamental power factor on phase 3 cosϕ3 | - | 0.0001 | 4598 | 11F6 | 2 | S32 | H'03' | Example: 0.2700: Hex 00 00 0A 8C
Minimum Total fundamental power factor cosϕtot | - | 0.0001 | 4600 | 11F8 | 2 | S32 | H'03' | Example: 0.1900: Hex 00 00 07 6C
Minimum Network frequency F | Hz | 0.001 | 4602 | 11FA | 2 | U32 | H'03' | Example: 49.840Hz: Hex 00 00 C2 B0
Minimum frequency Timestamp machine | s | 1 | 4604 | 11FC | 2 | U32 | H'03' | Example: 15600661s: Hex 00 EE 0C 15
Minimum frequency Timestamp user | s | 1 | 4606 | 11FE | 2 | U32 | H'03' | Example: 3556519s: Hex 00 36 44 A7
Minimum THD of U12 | % | 0.1 | 4608 | 1200 | 2 | U32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Minimum THD of U23 | % | 0.1 | 4610 | 1202 | 2 | U32 | H'03' | Example: 0.2%: Hex 00 00 00 02
Minimum THD of U31 | % | 0.1 | 4612 | 1204 | 2 | U32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Minimum THD of V1N | % | 0.1 | 4614 | 1206 | 2 | U32 | H'03' | Example: 0.6%: Hex 00 00 00 06
Minimum THD of V2N | % | 0.1 | 4616 | 1208 | 2 | U32 | H'03' | Example: 0.4%: Hex 00 00 00 04
Minimum THD of V3N | % | 0.1 | 4618 | 120A | 2 | U32 | H'03' | Example: 0.5%: Hex 00 00 00 05
Minimum THD of I1 | % | 0.1 | 4620 | 120C | 2 | U32 | H'03' | Example: 0.2%: Hex 00 00 00 02
Minimum THD of I2 | % | 0.1 | 4622 | 120E | 2 | U32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Minimum THD of I3 | % | 0.1 | 4624 | 1210 | 2 | U32 | H'03' | Example: 0.6%: Hex 00 00 00 06
Minimum of Maximun THD between I1, I2 & I3 | % | 0.1 | 4626 | 1212 | 2 | U32 | H'03' | Example: 0.4%: Hex 00 00 00 04
Maximum Phase to phase voltage U12 | V | 0.001 | 4628 | 1214 | 2 | U32 | H'03' | Example: 425.700V: Hex 00 06 7E E4
Maximum U12 Timestamp machine | s | 1 | 4630 | 1216 | 2 | U32 | H'03' | Example: 26153942s: Hex 01 8F 13 D6
Maximum U12 imestamp user | s | 1 | 4632 | 1218 | 2 | U32 | H'03' | Example: 14109800s: Hex 00 D7 4C 68
Maximum Phase to phase voltage U23 | V | 0.001 | 4634 | 121A | 2 | U32 | H'03' | Example: 425.500V: Hex 00 06 7E 1C
Maximum U23 Timestamp machine | s | 1 | 4636 | 121C | 2 | U32 | H'03' | Example: 26153942s: Hex 01 8F 13 D6
Maximum U23 Timestamp user | s | 1 | 4638 | 121E | 2 | U32 | H'03' | Example: 14109800s: Hex 00 D7 4C 68
Maximum Phase to phase voltage U31 | V | 0.001 | 4640 | 1220 | 2 | U32 | H'03' | Example: 424.200V: Hex 00 06 79 08
Maximum U31 Timestamp machine | s | 1 | 4642 | 1222 | 2 | U32 | H'03' | Example: 26153942s: Hex 01 8F 13 D6
Maximum U31 Timestamp user | s | 1 | 4644 | 1224 | 2 | U32 | H'03' | Example: 14109800s: Hex 00 D7 4C 68
Maximum Phase to neutral volatge V1N | V | 0.001 | 4646 | 1226 | 2 | U32 | H'03' | Example: 245.200V: Hex 00 03 BD D0
Maximum V1N Timestamp machine | s | 1 | 4648 | 1228 | 2 | U32 | H'03' | Example: 26153942s: Hex 01 8F 13 D6
Maximum V1N Timestamp user | s | 1 | 4650 | 122A | 2 | U32 | H'03' | Example: 14109800s: Hex 00 D7 4C 68
Maximum Phase to neutral volatge V2N | V | 0.001 | 4652 | 122C | 2 | U32 | H'03' | Example: 246.100V: Hex 00 03 C1 54
Maximum V2N Timestamp machine | s | 1 | 4654 | 122E | 2 | U32 | H'03' | Example: 26153958s: Hex 01 8F 13 E6
Maximum V2N Timestamp user | s | 1 | 4656 | 1230 | 2 | U32 | H'03' | Example: 14109816s: Hex 00 D7 4C 78
Maximum Phase to neutral volatge V3N | V | 0.001 | 4658 | 1232 | 2 | U32 | H'03' | Example: 245.100V: Hex 00 03 BD 6C
Maximum V3N Timestamp machine | s | 1 | 4660 | 1234 | 2 | U32 | H'03' | Example: 26153942s: Hex 01 8F 13 D6
Maximum V3N Timestamp user | s | 1 | 4662 | 1236 | 2 | U32 | H'03' | Example: 14109800s: Hex 00 D7 4C 68
Maximum Arithmetic average of U12, U23 & U31 : (U12+U23+U31) / 3 = Umoy L-L. | V | 0.001 | 4664 | 1238 | 2 | U32 | H'03' | Example: 425.100V: Hex 00 06 7C 8C
Maximum Arithmetic average of V1N, V2N & V3N : (V1N+V2N+V3N) / 3 = Vmoy L-N | V | 0.001 | 4666 | 123A | 2 | U32 | H'03' | Example: 245.400V: Hex 00 03 BE 98
Maximum unbalanced U12 vs Umoy L-L | % | 0.1 | 4668 | 123C | 2 | S32 | H'03' | Example: 11.1%: Hex 00 00 00 6F
Maximum unbalanced U23 vs Umoy L-L | % | 0.1 | 4670 | 123E | 2 | S32 | H'03' | Example: 1.8%: Hex 00 00 00 12
Maximum unbalanced U31 vs Umoy L-L | % | 0.1 | 4672 | 1240 | 2 | S32 | H'03' | Example: -9.7%: Hex FF FF FF 9F
Maximum of Maximum unbalanced composite voltage | % | 0.1 | 4674 | 1242 | 2 | S32 | H'03' | Example: 11.1%: Hex 00 00 00 6F
Maximum unbalanced V1N vs Vmoy L-N | % | 0.1 | 4676 | 1244 | 2 | S32 | H'03' | Example: 3.0%: Hex 00 00 00 1E
Maximum unbalanced V2N vs Vmoy L-N | % | 0.1 | 4678 | 1246 | 2 | S32 | H'03' | Example: 9.8%: Hex 00 00 00 62
Maximum unbalanced V3N vs Vmoy L-N | % | 0.1 | 4680 | 1248 | 2 | S32 | H'03' | Example: -12.9%: Hex FF FF FF 7F
Maximum Max unbalanced simple voltage | % | 0.1 | 4682 | 124A | 2 | S32 | H'03' | Example: -12.9%: Hex FF FF FF 7F
Maximum Current on phase 1: I1 | A | 0.001 | 4684 | 124C | 2 | U32 | H'03' | Example: 45.900A: Hex 00 00 B3 4C
Maximum I1 Timestamp machine | s | 1 | 4686 | 124E | 2 | U32 | H'03' | Example: 17056819s: Hex 01 04 44 33
Maximum I1 Timestamp user | s | 1 | 4688 | 1250 | 2 | U32 | H'03' | Example: 5012677s: Hex 00 4C 7C C5
Maximum Current on phase 2: I2 | A | 0.001 | 4690 | 1252 | 2 | U32 | H'03' | Example: 44.600A: Hex 00 00 AE 38
Maximum I2 Timestamp machine | s | 1 | 4692 | 1254 | 2 | U32 | H'03' | Example: 17056819s: Hex 01 04 44 33
Maximum I2 Timestamp user | s | 1 | 4694 | 1256 | 2 | U32 | H'03' | Example: 5012677s: Hex 00 4C 7C C5
Maximum Current on phase 3: I3 | A | 0.001 | 4696 | 1258 | 2 | U32 | H'03' | Example: 44.800A: Hex 00 00 AF 00
Maximum I3 Timestamp machine | s | 1 | 4698 | 125A | 2 | U32 | H'03' | Example: 17056819s: Hex 01 04 44 33
Maximum I3 Timestamp user | s | 1 | 4700 | 125C | 2 | U32 | H'03' | Example: 5012677s: Hex 00 4C 7C C5
Maximum Current on neutral: IN | A | 0.001 | 4702 | 125E | 2 | U32 | H'03' | Example: 10.200A: Hex 00 00 27 D8
Maximum IN Timestamp machine | s | 1 | 4704 | 1260 | 2 | U32 | H'03' | Example: 15074021s: Hex 00 E6 02 E5
Maximum IN Timestamp user | s | 1 | 4706 | 1262 | 2 | U32 | H'03' | Example: 3029879s: Hex 00 2E 3B 77
Maximum value of the calculated current IG | A | 0.001 | 4708 | 1264 | 2 | U32 | H'03' | Example: 44.800A: Hex 00 00 AF 00
Maximum of Maximum de I1, I2, I3 et IN | A | 0.001 | 4710 | 1266 | 2 | U32 | H'03' | Example: 45.900A: Hex 00 00 B3 4C
Maximum of Minimum of I1, I2 et I3 | A | 0.001 | 4712 | 1268 | 2 | U32 | H'03' | Example: 44.600A: Hex 00 00 AE 38
Maximum Arithmetic average of I1, I2 & I3 : (I1+I2+I3) / 3 = Imoy | A | 0.001 | 4714 | 126A | 2 | U32 | H'03' | Example: 45.100A: Hex 00 00 B0 2C
Maximum unbalanced I1 vs Imoy | % | 0.1 | 4716 | 126C | 2 | S32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Maximum unbalanced I2 vs Imoy | % | 0.1 | 4718 | 126E | 2 | S32 | H'03' | Example: 0.2%: Hex 00 00 00 02
Maximum unbalanced I3 vs Imoy | % | 0.1 | 4720 | 1270 | 2 | S32 | H'03' | Example: 0.3%: Hex 00 00 00 03
Maximum unbalanced IN vs Imoy | % | 0.1 | 4722 | 1272 | 2 | S32 | H'03' | Example: 0.5%: Hex 00 00 00 05
Maximum of maximum unbalanced current | % | 0.1 | 4724 | 1274 | 2 | S32 | H'03' | Example: 0.0%: Hex 00 00 00 00
Maximum Active power on phase 1 P1 | W | 1 | 4726 | 1276 | 2 | S32 | H'03' | Example: 9300W: Hex 00 00 24 54
Maximum Active power on phase 2 P2 | W | 1 | 4728 | 1278 | 2 | S32 | H'03' | Example: 9000W: Hex 00 00 23 28
Maximum Active power on phase 3 P3 | W | 1 | 4730 | 127A | 2 | S32 | H'03' | Example: 9000W: Hex 00 00 23 28
Maximum Total active power Ptot | W | 1 | 4732 | 127C | 2 | S32 | H'03' | Example: 27300W: Hex 00 00 6A A4
Maximum Reactive power on phase 1 Q1 | var | 1 | 4734 | 127E | 2 | S32 | H'03' | Example: 5700var: Hex 00 00 16 44
Maximum Reactive power on phase 2 Q2 | var | 1 | 4736 | 1280 | 2 | S32 | H'03' | Example: 5700var: Hex 00 00 16 44
Maximum Reactive power on phase 3 Q3 | var | 1 | 4738 | 1282 | 2 | S32 | H'03' | Example: 5700var: Hex 00 00 16 44
Maximum Total reactive power Qtot | var | 1 | 4740 | 1284 | 2 | S32 | H'03' | Example: 17100var: Hex 00 00 42 CC
Maximum Apparent power on phase 1 S1 | VA | 1 | 4742 | 1286 | 2 | U32 | H'03' | Example: 10700VA: Hex 00 00 29 CC
Maximum Apparent power on phase 2 S2 | VA | 1 | 4744 | 1288 | 2 | U32 | H'03' | Example: 10500VA: Hex 00 00 29 04
Maximum Apparent power on phase 3 S3 | VA | 1 | 4746 | 128A | 2 | U32 | H'03' | Example: 10400VA: Hex 00 00 28 A0
Maximum Total apparent power Stot | VA | 1 | 4748 | 128C | 2 | U32 | H'03' | Example: 31500VA: Hex 00 00 7B 0C
Maximum Power factor on phase 1 PF1 | - | 0.0001 | 4750 | 128E | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Power factor on phase 2 PF2 | - | 0.0001 | 4752 | 1290 | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Power factor on phase 3 PF3 | - | 0.0001 | 4754 | 1292 | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Total power factor PFtot | - | 0.0001 | 4756 | 1294 | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Fundamental power factor on phase 1 cosϕ1 | - | 0.0001 | 4758 | 1296 | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Fundamental power factor on phase 2 cosϕ2 | - | 0.0001 | 4760 | 1298 | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Fundamental power factor on phase 3 cosϕ3 | - | 0.0001 | 4762 | 129A | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Total fundamental power factor cosϕtot | - | 0.0001 | 4764 | 129C | 2 | S32 | H'03' | Example: 1.0000: Hex 00 00 27 10
Maximum Network frequency F | Hz | 0.001 | 4766 | 129E | 2 | U32 | H'03' | Example: 50.150Hz: Hex 00 00 C3 E6
Maximum Frequency Timestamp machine | s | 1 | 4768 | 12A0 | 2 | U32 | H'03' | Example: 27126744s: Hex 01 9D EB D8
Maximum Frequency Timestamp user | s | 1 | 4770 | 12A2 | 2 | U32 | H'03' | Example: 15082602s: Hex 00 E6 24 6A
Maximum THD of U12 | % | 0.1 | 4772 | 12A4 | 2 | U32 | H'03' | Example: 6.5%: Hex 00 00 00 41
Maximum THD of U23 | % | 0.1 | 4774 | 12A6 | 2 | U32 | H'03' | Example: 5.4%: Hex 00 00 00 36
Maximum THD of U31 | % | 0.1 | 4776 | 12A8 | 2 | U32 | H'03' | Example: 5.7%: Hex 00 00 00 39
Maximum THD of V1N | % | 0.1 | 4778 | 12AA | 2 | U32 | H'03' | Example: 7.1%: Hex 00 00 00 47
Maximum THD of V2N | % | 0.1 | 4780 | 12AC | 2 | U32 | H'03' | Example: 7.1%: Hex 00 00 00 47
Maximum THD of V3N | % | 0.1 | 4782 | 12AE | 2 | U32 | H'03' | Example: 4.3%: Hex 00 00 00 2B
Maximum THD of I1 | % | 0.1 | 4784 | 12B0 | 2 | U32 | H'03' | Example: 50.3%: Hex 00 00 01 F7
Maximum THD of I2 | % | 0.1 | 4786 | 12B2 | 2 | U32 | H'03' | Example: 77.3%: Hex 00 00 03 05
Maximum THD of I3 | % | 0.1 | 4788 | 12B4 | 2 | U32 | H'03' | Example: 68.6%: Hex 00 00 02 AE
Maximum of Maximun THD between I1, I2 & I3 | % | 0.1 | 4790 | 12B6 | 2 | U32 | H'03' | Example: 77.3%: Hex 00 00 03 05
Absolute active energy Ea | Wh | 1 | 4792 | 12B8 | 4 | U64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80
Net active energy Ea | Wh | 1 | 4796 | 12BC | 4 | S64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80
Direct active energy EaIn | Wh | 1 | 4800 | 12C0 | 4 | U64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80
Reverse active energy EaOut | Wh | 1 | 4804 | 12C4 | 4 | U64 | H'03' | Example: 14Wh: Hex 00 00 00 00 00 00 00 0E
Direct active energy EaIn (non resettable) | Wh | 1 | 4808 | 12C8 | 4 | U64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80
Reverse active energy EaOut (non resettable) | Wh | 1 | 4812 | 12CC | 4 | U64 | H'03' | Example: 14Wh: Hex 00 00 00 00 00 00 00 0E
Absolute Reactive energy Er | VArh | 1 | 4816 | 12D0 | 4 | U64 | H'03' | Example: 56984000VArh: Hex 00 00 00 00 03 65 81 C0
Net reactive energy Er | VArh | 1 | 4820 | 12D4 | 4 | S64 | H'03' | Example: 56984000VArh: Hex 00 00 00 00 03 65 81 C0
Direct reactive energy ErIn | VArh | 1 | 4824 | 12D8 | 4 | U64 | H'03' | Example: 56984000VArh: Hex 00 00 00 00 03 65 81 C0
Reverse reactive energy ErOut | VArh | 1 | 4828 | 12DC | 4 | U64 | H'03' | Example: 15VArh: Hex 00 00 00 00 00 00 00 0F
Apparente energy Es | VAh | 1 | 4832 | 12E0 | 4 | U64 | H'03' | Example: 68713000VAh: Hex 00 00 00 00 04 18 7A 28
On demand current on phase 1: I1 Dmd | A | 0.001 | 4836 | 12E4 | 2 | U32 | H'03' | Example: 15.000A: Hex 00 00 3A 98
On demand current on phase 2: I2 Dmd | A | 0.001 | 4838 | 12E6 | 2 | U32 | H'03' | Example: 14.000A: Hex 00 00 36 B0
On demand current on phase 3: I3 Dmd | A | 0.001 | 4840 | 12E8 | 2 | U32 | H'03' | Example: 14.000A: Hex 00 00 36 B0
On demand current on neutral: IN Dmd | A | 0.001 | 4842 | 12EA | 2 | U32 | H'03' | Example: 0.200A: Hex 00 00 00 C8
On demand current Imoy: Imoy Dmd | A | 0.001 | 4844 | 12EC | 2 | U32 | H'03' | Example: 14.300A: Hex 00 00 37 DC
Maximum On demand current on phase 1: I1 max Dmd | A | 0.001 | 4846 | 12EE | 2 | U32 | H'03' | Example: 20.400A: Hex 00 00 4F B0
Maximum On demand current on phase 2: I2 max Dmd | A | 0.001 | 4848 | 12F0 | 2 | U32 | H'03' | Example: 19.300A: Hex 00 00 4B 64
Maximum On demand current on phase 3: I3 max Dmd | A | 0.001 | 4850 | 12F2 | 2 | U32 | H'03' | Example: 19.900A: Hex 00 00 4D BC
Maximum On demand current on neutral: IN max Dmd | A | 0.001 | 4852 | 12F4 | 2 | U32 | H'03' | Example: 2.300A: Hex 00 00 08 FC
Maximum On demand current Imoy: Imoy max Dmd | A | 0.001 | 4854 | 12F6 | 2 | U32 | H'03' | Example: 19.800A: Hex 00 00 4D 58
On demand active power on phase 1: P1 Dmd | W | 1 | 4856 | 12F8 | 2 | S32 | H'03' | Example: 2000W: Hex 00 00 07 D0
On demand active power on phase 2: P2 Dmd | W | 1 | 4858 | 12FA | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
On demand active power on phase 3: P3 Dmd | W | 1 | 4860 | 12FC | 2 | S32 | H'03' | Example: 1600W: Hex 00 00 06 40
On demand total active power: Ptot Dmd | W | 1 | 4862 | 12FE | 2 | S32 | H'03' | Example: 5200W: Hex 00 00 14 50
Maximum On demand active power on phase 1: P1 Dmd | W | 1 | 4864 | 1300 | 2 | S32 | H'03' | Example: 3700W: Hex 00 00 0E 74
Maximum On demand active power on phase 2: P2 Dmd | W | 1 | 4866 | 1302 | 2 | S32 | H'03' | Example: 3400W: Hex 00 00 0D 48
Maximum On demand active power on phase 3: P3 Dmd | W | 1 | 4868 | 1304 | 2 | S32 | H'03' | Example: 3500W: Hex 00 00 0D AC
Maximum On demand total active power: Ptot Dmd | W | 1 | 4870 | 1306 | 2 | S32 | H'03' | Example: 10500W: Hex 00 00 29 04
On demand reactive power on phase 1: Q1 Dmd | var | 1 | 4872 | 1308 | 2 | S32 | H'03' | Example: 2800var: Hex 00 00 0A F0
On demand reactive power on phase 2: Q2 Dmd | var | 1 | 4874 | 130A | 2 | S32 | H'03' | Example: 2800var: Hex 00 00 0A F0
On demand reactive power on phase 3: Q3 Dmd | var | 1 | 4876 | 130C | 2 | S32 | H'03' | Example: 2800var: Hex 00 00 0A F0
On demand total reactive power: Qtot Dmd | var | 1 | 4878 | 130E | 2 | S32 | H'03' | Example: 8500var: Hex 00 00 21 34
Maximum On demand reactive power on phase 1: Q1 Dmd | var | 1 | 4880 | 1310 | 2 | S32 | H'03' | Example: 3200var: Hex 00 00 0C 80
Maximum On demand reactive power on phase 2: Q2 Dmd | var | 1 | 4882 | 1312 | 2 | S32 | H'03' | Example: 3200var: Hex 00 00 0C 80
Maximum On demand reactive power on phase 3: Q3 Dmd | var | 1 | 4884 | 1314 | 2 | S32 | H'03' | Example: 3200var: Hex 00 00 0C 80
Maximum On demand tttal reactive power: Qtot Dmd | var | 1 | 4886 | 1316 | 2 | S32 | H'03' | Example: 9500var: Hex 00 00 25 1C
On demand apparent power on phase 1: S1 Dmd | VA | 1 | 4888 | 1318 | 2 | U32 | H'03' | Example: 3500VA: Hex 00 00 0D AC
On demand apparent power on phase 2: S2 Dmd | VA | 1 | 4890 | 131A | 2 | U32 | H'03' | Example: 3300VA: Hex 00 00 0C E4
On demand apparent power on phase 3: S3 Dmd | VA | 1 | 4892 | 131C | 2 | U32 | H'03' | Example: 3200VA: Hex 00 00 0C 80
On demand total apparrent power: Stot Dmd | VA | 1 | 4894 | 131E | 2 | U32 | H'03' | Example: 10000VA: Hex 00 00 27 10
Maximum On demand apparent power on phase 1: S1 Dmd | VA | 1 | 4896 | 1320 | 2 | U32 | H'03' | Example: 4800VA: Hex 00 00 12 C0
Maximum On demand apparent power on phase 2: S2 Dmd | VA | 1 | 4898 | 1322 | 2 | U32 | H'03' | Example: 4600VA: Hex 00 00 11 F8
Maximum On demand apparent power on phase 3: S3 Dmd | VA | 1 | 4900 | 1324 | 2 | U32 | H'03' | Example: 4700VA: Hex 00 00 12 5C
Maximum On demand total apparent power: Stot Dmd | VA | 1 | 4902 | 1326 | 2 | U32 | H'03' | Example: 14100VA: Hex 00 00 37 14
Operating quadrant | - | 1 | 4904 | 1328 | 1 | U16 | H'03' | Example: 1: Hex 00 01
Phase rotation | - | 1 | 4905 | 1329 | 1 | U16 | H'03' | Example: 1: Hex 00 01
Reset I_min/max Timestamp machine | s | 1 | 4906 | 132A | 2 | U32 | H'03' | Example: 34915975s: Hex 02 14 C6 87
Reset I_min/max Timestamp user | s | 1 | 4908 | 132C | 2 | U32 | H'03' | Example: 34915975s: Hex 02 14 C6 87
Reset V_min/maxTimestamp machine | s | 1 | 4910 | 132E | 2 | U32 | H'03' | -
Reset V_min/max Timestamp user | s | 1 | 4912 | 1330 | 2 | U32 | H'03' | -
Reset P_min/max Timestamp machine | s | 1 | 4914 | 1332 | 2 | U32 | H'03' | -
Reset P_min/max Timestamp user | s | 1 | 4916 | 1334 | 2 | U32 | H'03' | -
Reset PF_min/max Timestamp machine | s | 1 | 4918 | 1336 | 2 | U32 | H'03' | -
Reset PF_min/max Timestamp user | s | 1 | 4920 | 1338 | 2 | U32 | H'03' | -
Reset THD_min/max Timestamp machine | s | 1 | 4922 | 133A | 2 | U32 | H'03' | -
Reset THD_min/max Timestamp user | s | 1 | 4924 | 133C | 2 | U32 | H'03' | -
Reset F_min/max Timestamp machine | s | 1 | 4926 | 133E | 2 | U32 | H'03' | -
Reset F_min/max Timestamp user | s | 1 | 4928 | 1340 | 2 | U32 | H'03' | -
Reset Energy counter Timestamp machine | s | 1 | 4930 | 1342 | 2 | U32 | H'03' | -
Reset Energy counter Timestamp user | s | 1 | 4932 | 1344 | 2 | U32 | H'03' | -
Reset IdmdMax Timestamp machine | s | 1 | 4934 | 1346 | 2 | U32 | H'03' | -
Reset IdmdMax Timestamp user | s | 1 | 4936 | 1348 | 2 | U32 | H'03' | -
Reset PQSDmdMax Timestamp machine | s | 1 | 4938 | 134A | 2 | U32 | H'03' | -
Reset PQSDmdMax Timestamp user | s | 1 | 4940 | 134C | 2 | U32 | H'03' | -

## Indicators
Indicators
Product reference | [7 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | Further information
AX status | - | - | 5376 | 1500 | 1 | U16 | H'03' | Hex 00 00 = AX contact is opened, Hex 00 01 = AX contact is closed.
AL status | - | - | 5377 | 1501 | 1 | U16 | H'03' | Hex 00 00 = AL contact is opened, Hex 00 01 = AL contact is closed.
Absolute counter of ON/OFF cycle | - | 1 | 5378 | 1502 | 1 | U16 | H'03' | Non resetable counter Example: 2: Hex 00 02
Absolute counter of electromechanical trip | - | 1 | 5379 | 1503 | 1 | U16 | H'03' | Non resetable counter Example: 2: Hex 00 02
Counter of ON/OFF cycle | - | 1 | 5380 | 1504 | 1 | U16 | H'03' | Resetable counter Example: 2: Hex 00 02
Counter of electromechanical trip | - | 1 | 5381 | 1505 | 1 | U16 | H'03' | Resetable counter Example: 2: Hex 00 02
Date & time synchronisation | - | 1 | 5382 | 1506 | 1 | U16 | H'03' | Hex 00 00 = not synchronised, Hex 00 01 = synchronised
Measurements availability status | - | - | 5385 | 1509 | 1 | U16 | H'03' | Hex 00 00 = False, Hex 00 01 = True
Custom alarms configuration status | - | - | 5386 | 150A | 1 | U16 | H'03' | Custom alarms configuration status on 12 Bits. Value 0: alarm not configured ; value 1: alarm configured bit 0 = custom alarm 1 bit 1 = custom alarm 2 bit 2 = custom alarm 3 bit 3 = custom alarm 4 bit 4 = custom alarm 5 bit 5 = custom alarm 6 bit 6 = custom alarm 7 bit 7 = custom alarm 8 bit 8 = custom alarm 9 bit 9 = custom alarm 10 bit 10 = custom alarm 11 bit 11 = custom alarm 12 Example: custom alarms 1 and 2 configured: Hex 00 03
Custom alarms status | - | - | 5387 | 150B | 1 | U16 | H'03' | Custom alarms status on 12 Bits. Value 0: alarm deactivated ; value 1: alarm activated bit 0 = custom alarm 1 bit 1 = custom alarm 2 bit 2 = custom alarm 3 bit 3 = custom alarm 4 bit 4 = custom alarm 5 bit 5 = custom alarm 6 bit 6 = custom alarm 7 bit 7 = custom alarm 8 bit 4 = custom alarm 9 bit 5 = custom alarm 10 bit 6 = custom alarm 11 bit 7 = custom alarm 12 Example: custom alarms 1 and 2 configured: Hex 00 03
Custom alarm max range | - | 1 | 5388 | 150C | 1 | U16 | H'03'
Trip alarms configuration status | - | - | 5390 | 150E | 1 | U16 | H'03' | Trip alarms configuration status on 5 Bits. Value 0: alarm not configured ; value 1: alarm configured bit 0 = Long time trip alarm bit 1 = Short time trip alarm bit 2 = Instantaneous trip alarm bit 3 = Ground fault trip alarm bit 4 = reserved bit 5 = Configuration tool test trip alarm Example: Long time trip alarm configured: Hex 00 01
Trip alarms status | - | - | 5391 | 150F | 1 | U16 | H'03' | Hex 00 00 = Alarm OFF, Hex 00 01 = Alarm ON
Overload prealarm PTA status | - | - | 5392 | 1510 | 1 | U16 | H'03' | Hex 00 00 = Alarm ends off, Hex 00 01 = Alarm occurs
PTA output contact status | - | - | 5393 | 1511 | 1 | U16 | H'03' | Hex 00 00 = contact is opened, Hex 00 01 = contact is closed.
OAC alarm status | - | - | 5394 | 1512 | 1 | U16 | H'03' | Hex 00 00 = Alarm ends off, Hex 00 01 = Alarm occurs
OAC output contact status | - | - | 5395 | 1513 | 1 | U16 | H'03' | Hex 00 00 = contact is opened, Hex 00 01 = contact is closed.
Trip unit internal temperature | °C | 1 | 5396 | 1514 | 1 | S16 | H'03' | Example: 40°C: Hex 00 28
Trip unit internal temperature alarm status | - | - | 5397 | 1515 | 1 | U16 | H'03' | Hex 00 00 = no alarm, Hex 00 01 = alarm ON
Short time ZSI1 input status | - | - | 5406 | 151E | 1 | U16 | H'03' | Hex 00 00 = no fault detected from downstream breakers, Hex 00 01 = fault detected from downstream breaker
Short time ZSI2 output status | - | - | 5407 | 151F | 1 | U16 | H'03' | Hex 00 00 = no fault detected, Hex 00 01 = fault detected
Ground fault ZSI1 input status | - | - | 5408 | 1520 | 1 | U16 | H'03' | Hex 00 00 = no fault detected from downstream breakers, Hex 00 01 = fault detected from downstream breaker
Ground fault ZSI2 output status | - | - | 5409 | 1521 | 1 | U16 | H'03' | Hex 00 00 = no fault detected, Hex 00 01 = fault detected
Operating time counter | s | 1 | 5410 | 1522 | 2 | U32 | H'03' | Example: 34915975s: Hex 02 14 C6 87
Trip unit error status | - | - | 5431 | 1537 | 1 | U16 | H'03' | Error status on 8 Bits. Value 0: no failure; value 1: failure. bit 0 = actuator error bit 1 = current sensor phase 1 error bit 2 = current sensor phase 2 error bit 3 = current sensor phase 3 error bit 4 = current sensor neutral error bit 5 = internal voltage error bit 6 = hardware fault bit 7 = software fault Example: actuator error and Software fault: Hex 00 81
Countdown before Long time trip | s | 1 | 5440 | 1540 | 1 | U16 | H'03' | Example: 7200s: Hex 1C 20
Counter of Long time trip alarm | INT | 1 | 5441 | 1541 | 1 | U16 | H'03' | Example: 5: Hex 00 05
Counter of Short time trip alarm | INT | 1 | 5442 | 1542 | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of Instantaneous trip alarm | INT | 1 | 5443 | 1543 | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of Ground fault trip alarm | INT | 1 | 5444 | 1544 | 1 | U16 | H'03' | Example: 1: Hex 00 01
Counter of configuration tool test trip | INT | 1 | 5445 | 1545 | 1 | U16 | H'03' | Example: 3: Hex 00 03
Counter of overload prealarm PTA | INT | 1 | 5446 | 1546 | 1 | U16 | H'03' | Example: 5: Hex 00 05
Counter of OAC alarm | INT | 1 | 5447 | 1547 | 1 | U16 | H'03' | Example: 15: Hex 00 0F
Counter of custom alarm n°1 | INT | 1 | 5448 | 1548 | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of custom alarm n°2 | INT | 1 | 5449 | 1549 | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of custom alarm n°3 | INT | 1 | 5450 | 154A | 1 | U16 | H'03' | Example: 1: Hex 00 01
Counter of custom alarm n°4 | INT | 1 | 5451 | 154B | 1 | U16 | H'03' | Example: 3: Hex 00 03
Counter of custom alarm n°5 | INT | 1 | 5452 | 154C | 1 | U16 | H'03' | Example: 5: Hex 00 05
Counter of custom alarm n°6 | INT | 1 | 5453 | 154D | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of custom alarm n°7 | INT | 1 | 5454 | 154E | 1 | U16 | H'03' | Example: 2: Hex 00 02
Counter of custom alarm n°8 | INT | 1 | 5455 | 154F | 1 | U16 | H'03' | Example: 1: Hex 00 01
Counter of custom alarm n°9 | INT | 1 | 5456 | 1550 | 1 | U16 | H'03' | Example: 3: Hex 00 03
Counter of custom alarm n°10 | INT | 1 | 5457 | 1551 | 1 | U16 | H'03' | Example: 5: Hex 00 05
Counter of custom alarm n°11 | INT | 1 | 5458 | 1552 | 1 | U16 | H'03' | Example: 3: Hex 00 03
Counter of custom alarm n°12 | INT | 1 | 5459 | 1553 | 1 | U16 | H'03' | Example: 5: Hex 00 05
MCCB Ready to protect | - | 1 | 5461 | 1555 | 1 | U16 | H'03' | Hex 00 00 = Trip unit OFF, Hex 00 01 = Trip unit not ready, Hex 00 02 = Trip unit ready
Trip unit internal error | - | 1 | 5462 | 1556 | 1 | U16 | H'03' | Hex 00 01 = Trip unit internal error
LED PTA status | - | 1 | 5463 | 1557 | 1 | U16 | H'03' | Hex 00 00 = No alarm, Hex 00 01 = PTA threshold reached, Hex 00 02 = PTA prelarm and PTA contact activated
LED > Ir status | - | 1 | 5464 | 1558 | 1 | U16 | H'03' | Hex 00 00 = no alarm, Hex 00 01 = I ≥ 105% Ir, Hex 00 02 = I ≥ 112% Ir

## History
History
Product reference | [7 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | Further information
Custom alarm storage 1: Custtom alarm ID | - | - | 5888 | 1700 | 1 | U16 | H'03' | Example: Custom alarm ID 42: Hex 00 2A
Custom alarm storage 1: Timestamp machine | s | 1 | 5889 | 1701 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Custom alarm storage 1: Timestamp user | s | 1 | 5891 | 1703 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Custom alarm storage 1: Event category | - | - | 5893 | 1705 | 1 | U16 | H'03' | Hex 00 00 = alarm occurs, Hex 00 01 = alarm cut off
Custom Alarm storage 2: 6 following registers, same as Custom alarm storage 1 | - | - | 5894 | 1706 | 6 | U16 | H'03' | -
Custom Alarm storage 3: 6 following registers, same as Custom alarm storage 1 | - | - | 5900 | 170C | 6 | U16 | H'03' | -
Custom Alarm storage 4: 6 following registers, same as Custom alarm storage 1 | - | - | 5906 | 1712 | 6 | U16 | H'03' | -
Custom Alarm storage 5: 6 following registers, same as Custom alarm storage 1 | - | - | 5912 | 1718 | 6 | U16 | H'03' | -
Custom Alarm storage 6: 6 following registers, same as Custom alarm storage 1 | - | - | 5918 | 171E | 6 | U16 | H'03' | -
Custom Alarm storage 7: 6 following registers, same as Custom alarm storage 1 | - | - | 5924 | 1724 | 6 | U16 | H'03' | -
Custom Alarm storage 8: 6 following registers, same as Custom alarm storage 1 | - | - | 5930 | 172A | 6 | U16 | H'03' | -
Custom Alarm storage 9: 6 following registers, same as Custom alarm storage 1 | - | - | 5936 | 1730 | 6 | U16 | H'03' | -
Custom Alarm storage 10: 6 following registers, same as Custom alarm storage 1 | - | - | 5942 | 1736 | 6 | U16 | H'03' | -
Custom Alarm storage 11: 6 following registers, same as Custom alarm storage 1 | - | - | 5948 | 173C | 6 | U16 | H'03' | -
Custom Alarm storage 12: 6 following registers, same as Custom alarm storage 1 | - | - | 5954 | 1742 | 6 | U16 | H'03' | -
Custom Alarm storage 13: 6 following registers, same as Custom alarm storage 1 | - | - | 5960 | 1748 | 6 | U16 | H'03' | -
Custom Alarm storage 14: 6 following registers, same as Custom alarm storage 1 | - | - | 5966 | 174E | 6 | U16 | H'03' | -
Custom Alarm storage 15: 6 following registers, same as Custom alarm storage 1 | - | - | 5972 | 1754 | 6 | U16 | H'03' | -
Custom Alarm storage 16: 6 following registers, same as Custom alarm storage 1 | - | - | 5978 | 175A | 6 | U16 | H'03' | -
Custom Alarm storage 17: 6 following registers, same as Custom alarm storage 1 | - | - | 5984 | 1760 | 6 | U16 | H'03' | -
Custom Alarm storage 18: 6 following registers, same as Custom alarm storage 1 | - | - | 5990 | 1766 | 6 | U16 | H'03' | -
Custom Alarm storage 19: 6 following registers, same as Custom alarm storage 1 | - | - | 5996 | 176C | 6 | U16 | H'03' | -
Custom Alarm storage 20: 6 following registers, same as Custom alarm storage 1 | - | - | 6002 | 1772 | 6 | U16 | H'03' | -
Custom Alarm storage 21: 6 following registers, same as Custom alarm storage 1 | - | - | 6008 | 1778 | 6 | U16 | H'03' | -
Custom Alarm storage 22: 6 following registers, same as Custom alarm storage 1 | - | - | 6014 | 177E | 6 | U16 | H'03' | -
Custom Alarm storage 23: 6 following registers, same as Custom alarm storage 1 | - | - | 6020 | 1784 | 6 | U16 | H'03' | -
Custom Alarm storage 24: 6 following registers, same as Custom alarm storage 1 | - | - | 6026 | 178A | 6 | U16 | H'03' | -
Custom Alarm storage 25: 6 following registers, same as Custom alarm storage 1 | - | - | 6032 | 1790 | 6 | U16 | H'03' | -
Custom Alarm storage 26: 6 following registers, same as Custom alarm storage 1 | - | - | 6038 | 1796 | 6 | U16 | H'03' | -
Custom Alarm storage 27: 6 following registers, same as Custom alarm storage 1 | - | - | 6044 | 179C | 6 | U16 | H'03' | -
Custom Alarm storage 28: 6 following registers, same as Custom alarm storage 1 | - | - | 6050 | 17A2 | 6 | U16 | H'03' | -
Custom Alarm storage 29: 6 following registers, same as Custom alarm storage 1 | - | - | 6056 | 17A8 | 6 | U16 | H'03' | -
Custom Alarm storage 30: 6 following registers, same as Custom alarm storage 1 | - | - | 6062 | 17AE | 6 | U16 | H'03' | -
Custom Alarm storage 31: 6 following registers, same as Custom alarm storage 1 | - | - | 6068 | 17B4 | 6 | U16 | H'03' | -
Custom Alarm storage 32: 6 following registers, same as Custom alarm storage 1 | - | - | 6074 | 17BA | 6 | U16 | H'03' | -
Custom Alarm storage 33: 6 following registers, same as Custom alarm storage 1 | - | - | 6080 | 17C0 | 6 | U16 | H'03' | -
Custom Alarm storage 34: 6 following registers, same as Custom alarm storage 1 | - | - | 6086 | 17C6 | 6 | U16 | H'03' | -
Custom Alarm storage 35: 6 following registers, same as Custom alarm storage 1 | - | - | 6092 | 17CC | 6 | U16 | H'03' | -
Custom Alarm storage 36: 6 following registers, same as Custom alarm storage 1 | - | - | 6098 | 17D2 | 6 | U16 | H'03' | -
Custom Alarm storage 37: 6 following registers, same as Custom alarm storage 1 | - | - | 6104 | 17D8 | 6 | U16 | H'03' | -
Custom Alarm storage 38: 6 following registers, same as Custom alarm storage 1 | - | - | 6110 | 17DE | 6 | U16 | H'03' | -
Custom Alarm storage 39: 6 following registers, same as Custom alarm storage 1 | - | - | 6116 | 17E4 | 6 | U16 | H'03' | -
Custom Alarm storage 40: 6 following registers, same as Custom alarm storage 1 | - | - | 5445 | 17EA | 6 | U16 | H'03' | -
Trip Alarm storage 1: Alarm ID | - | - | 6128 | 17F0 | 1 | U16 | H'03' | Example: Alarm ID 12: Hex 00 0C
Trip Alarm storage 1:Timestamp machine | s | 1 | 6129 | 17F1 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Trip Alarm storage 1:Timestamp user | s | 1 | 6131 | 17F3 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Trip Alarm storage 1:Fault duration | s | 1 | 6133 | 17F5 | 1 | U16 | H'03' | Example: 160s: Hex 00 00 00 A1
Trip Alarm storage 1:Complementary information | A | 1 | 6134 | 17F6 | 1 | U16 | H'03' | Example: 20000A: Hex 4E 20
Trip Alarm storage 2: 7 following registers, same as Trip alarm storage 1 | - | - | 6135 | 17F7 | 7 | U16 | H'03' | -
Trip Alarm storage 3: 7 following registers, same as Trip alarm storage 1 | - | - | 6142 | 17FE | 7 | U16 | H'03' | -
Trip Alarm storage 4: 7 following registers, same as Trip alarm storage 1 | - | - | 6149 | 1805 | 7 | U16 | H'03' | -
Trip Alarm storage 5: 7 following registers, same as Trip alarm storage 1 | - | - | 6156 | 180C | 7 | U16 | H'03' | -
Trip Alarm storage 6: 7 following registers, same as Trip alarm storage 1 | - | - | 6163 | 1813 | 7 | U16 | H'03' | -
Trip Alarm storage 7: 7 following registers, same as Trip alarm storage 1 | - | - | 6170 | 181A | 7 | U16 | H'03' | -
Trip Alarm storage 8: 7 following registers, same as Trip alarm storage 1 | - | - | 6177 | 1821 | 7 | U16 | H'03' | -
Trip Alarm storage 9: 7 following registers, same as Trip alarm storage 1 | - | - | 6184 | 1828 | 7 | U16 | H'03' | -
Trip Alarm storage 10: 7 following registers, same as Trip alarm storage 1 | - | - | 6191 | 182F | 7 | U16 | H'03' | -
Last trip event Alarm ID | - | - | 6198 | 1836 | 1 | U16 | H'03' | Example: Alarm ID 12: Hex 00 0C
Last trip event timestamp machine | s | 1 | 6199 | 1837 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Last trip event timestamp user | s | 1 | 6201 | 1839 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Last trip event fault duration | s | 1 | 6203 | 183B | 1 | U16 | H'03' | Example: 160s: Hex 00 00 00 A1
Last trip event complemantary information | A | 1 | 6204 | 183C | 1 | U16 | H'03' | Example: 20000A: Hex 4E 20
Ir setting storage 1: Previous Ir setting | A | 1 | 6205 | 183D | 1 | U16 | H'03' | Example: 160A: Hex 00 A0
Ir setting storage 1: Timestamp machine | s | 1 | 6206 | 183E | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ir setting storage 1: Timestamp user | s | 1 | 6208 | 1840 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ir setting storage 2: 5 following registers, same as Trip alarm storage 1 | - | - | 6210 | 1842 | 5 | U16 | H'03' | -
Ir setting storage 3: 5 following registers, same as Trip alarm storage 1 | - | - | 6215 | 1847 | 5 | U16 | H'03' | -
Ir setting storage 4: 5 following registers, same as Trip alarm storage 1 | - | - | 6220 | 184C | 5 | U16 | H'03' | -
Ir setting storage 5: 5 following registers, same as Trip alarm storage 1 | - | - | 6225 | 1851 | 5 | U16 | H'03' | -
tr setting storage 1: Previous tr time delay | s | 0.25 | 6230 | 1856 | 1 | U16 | H'03' | Example: 5s: Hex 00 14
tr setting storage 1: Timestamp machine | s | 1 | 6231 | 1857 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
tr setting storage 1: Timestamp user | s | 1 | 6233 | 1859 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
tr setting storage 2: 5 following registers, same as tr setting storage 1 | - | - | 6235 | 185B | 5 | U16 | H'03' | -
tr setting storage 3: 5 following registers, same as tr setting storage 1 | - | - | 6240 | 1860 | 5 | U16 | H'03' | -
tr setting storage 4: 5 following registers, same as tr setting storage 1 | - | - | 6245 | 1865 | 5 | U16 | H'03' | -
tr setting storage 5: 5 following registers, same as tr setting storage 1 | - | - | 6250 | 186A | 5 | U16 | H'03' | -
Isd protection status setting storage 1: Previous Isd protection status | - | - | 6255 | 186F | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Isd protection status setting storage 1: Timestamp machine | s | 1 | 6256 | 1870 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Isd protection status setting storage 1: Timestamp user | s | 1 | 6258 | 1872 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Isd protection status setting storage 2: 5 following registers, same as Isd protection status setting storage 1 | - | - | 6260 | 1874 | 5 | U16 | H'03' | -
Isd protection status setting storage 3: 5 following registers, same as Isd protection status setting storage 1 | - | - | 6265 | 1879 | 5 | U16 | H'03' | -
Isd protection status setting storage 4: 5 following registers, same as Isd protection status setting storage 1 | - | - | 6270 | 187E | 5 | U16 | H'03' | -
Isd protection status setting storage 5: 5 following registers, same as Isd protection status setting storage 1 | - | - | 6275 | 1883 | 5 | U16 | H'03' | -
Isd setting storage 1: Previous Isd setting | x Isd | 0.5 | 6280 | 1888 | 1 | U16 | H'03' | Example: 5 x Isd: Hex 00 14
Isd setting storage 1: Timestamp machine | s | 1 | 6281 | 1889 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Isd setting storage 1: Timestamp user | s | 1 | 6283 | 188B | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Isd setting storage 2: 5 following registers, same as Isd setting storage 1 | - | - | 6285 | 188D | 5 | U16 | H'03' | -
Isd setting storage 3: 5 following registers, same as Isd setting storage 1 | - | - | 6290 | 1892 | 5 | U16 | H'03' | -
Isd setting storage 4: 5 following registers, same as Isd setting storage 1 | - | - | 6295 | 1897 | 5 | U16 | H'03' | -
Isd setting storage 5: 5 following registers, same as Isd setting storage 1 | - | - | 6300 | 189C | 5 | U16 | H'03' | -
tsd setting storage 1: Previous tsd time delay | ms | NA | 6305 | 18A1 | 1 | U16 | H'03' | Example: 300ms: Hex 01 2C
tsd setting storage 1: Timestamp machine | s | 1 | 6306 | 18A2 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
tsd setting storage 1: Timestamp user | s | 1 | 6308 | 18A4 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
tsd setting storage 2: 5 following registers, same as tsd setting storage 1 | - | - | 6310 | 18A6 | 5 | U16 | H'03' | -
tsd setting storage 3: 5 following registers, same as tsd setting storage 1 | - | - | 6315 | 18AB | 5 | U16 | H'03' | -
tsd setting storage 4: 5 following registers, same as tsd setting storage 1 | - | - | 6320 | 18B0 | 5 | U16 | H'03' | -
tsd setting storage 5: 5 following registers, same as tsd setting storage 1 | - | - | 6325 | 18B5 | 5 | U16 | H'03' | -
Short i²t setting storage 1: Previous i²t | - | - | 6330 | 18BA | 1 | U16 | H'03' | Hex 00 00 = I²t disable, Hex 00 01 = I²t enable
Short i²t setting storage 1: Timestamp machine | s | 1 | 6331 | 18BB | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Short i²t setting storage 1: Timestamp user | s | 1 | 6333 | 18BD | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Short i²t setting storage 2: 5 following registers, same as Short i²t setting storage 1 | - | - | 6335 | 18BF | 5 | U16 | H'03' | -
Short i²t setting storage 3: 5 following registers, same as Short i²t setting storage 1 | - | - | 6340 | 18C4 | 5 | U16 | H'03' | -
Short i²t setting storage 4: 5 following registers, same as Short i²t setting storage 1 | - | - | 6345 | 18C9 | 5 | U16 | H'03' | -
Short i²t setting storage 5: 5 following registers, same as Short i²t setting storage 1 | - | - | 6350 | 18CE | 5 | U16 | H'03' | -
Ii setting storage 1: Previous Ii setting | x In | 1 | 6355 | 18D3 | 1 | U16 | H'03' | Example: 15 x In: Hex 00 0F
Ii setting storage 1: Timestamp machine | s | 1 | 6356 | 18D4 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ii setting storage 1: Timestamp user | s | 1 | 6358 | 18D6 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ii setting storage 2: 5 following registers, same as Ii setting storage 1 | - | - | 6360 | 18D8 | 5 | U16 | H'03' | -
Ii setting storage 3: 5 following registers, same as Ii setting storage 1 | - | - | 6365 | 18DD | 5 | U16 | H'03' | -
Ii setting storage 4: 5 following registers, same as Ii setting storage 1 | - | - | 6370 | 18E2 | 5 | U16 | H'03' | -
Ii setting storage 5: 5 following registers, same as Ii setting storage 1 | - | - | 6375 | 18E7 | 5 | U16 | H'03' | -
Ig protection status setting storage 1: Previous Ig protection status | - | - | 6380 | 18EC | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Ig protection status setting storage 1: Timestamp machine | s | 1 | 6381 | 18ED | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ig protection status setting storage 1: Timestamp user | s | 1 | 6383 | 18EF | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ig protection status setting storage 2: 5 following registers, same as Ig protection status setting storage 1 | - | - | 6385 | 18F1 | 5 | U16 | H'03' | -
Ig protection status setting storage 3: 5 following registers, same as Ig protection status setting storage 1 | - | - | 6390 | 18F6 | 5 | U16 | H'03' | -
Ig protection status setting storage 4: 5 following registers, same as Ig protection status setting storage 1 | - | - | 6395 | 18FB | 5 | U16 | H'03' | -
Ig protection status setting storage 5: 5 following registers, same as Ig protection status setting storage 1 | - | - | 6400 | 1900 | 5 | U16 | H'03' | -
Ig setting storage 1: Previous Ig setting | x In | - | 6405 | 1905 | 1 | U16 | H'03' | Example: 0.2 x In: Hex 00 04
Ig setting storage 1: Timestamp machine | s | 1 | 6406 | 1906 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ig setting storage 1: Timestamp user | s | 1 | 6408 | 1908 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ig setting storage 2: 5 following registers, same as Ig setting storage 1 | - | - | 6410 | 190A | 5 | U16 | H'03' | -
Ig setting storage 3: 5 following registers, same as Ig setting storage 1 | - | - | 6415 | 190F | 5 | U16 | H'03' | -
Ig setting storage 4: 5 following registers, same as Ig setting storage 1 | - | - | 6420 | 1914 | 5 | U16 | H'03' | -
Ig setting storage 5: 5 following registers, same as Ig setting storage 1 | - | - | 6425 | 1919 | 5 | U16 | H'03' | -
tg setting storage 1: Previous tg time delay | ms | NA | 6430 | 191E | 1 | U16 | H'03' | Example: 300ms: Hex 01 2C
tg setting storage 1: Timestamp machine | s | 1 | 6431 | 191F | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
tg setting storage 1: Timestamp user | s | 1 | 6433 | 1921 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
tg setting storage 2: 5 following registers, same as tg setting storage 1 | - | - | 6435 | 1923 | 5 | U16 | H'03' | -
tg setting storage 3: 5 following registers, same as tg setting storage 1 | - | - | 6440 | 1928 | 5 | U16 | H'03' | -
tg setting storage 4: 5 following registers, same as tg setting storage 1 | - | - | 6445 | 192D | 5 | U16 | H'03' | -
tg setting storage 5: 5 following registers, same as tg setting storage 1 | - | - | 6450 | 1932 | 5 | U16 | H'03' | -
Ground i²t setting storage 1: Previous i²t | - | - | 6455 | 1937 | 1 | U16 | H'03' | Hex 00 00 = I²t disable, Hex 00 01 = I²t enable
Ground i²t setting storage 1: Timestamp machine | s | 1 | 6456 | 1938 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ground i²t setting storage 1: Timestamp user | s | 1 | 6458 | 193A | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ground i²t setting storage 2: 5 following registers, same as Ground i²t setting storage 1 | - | - | 6460 | 193C | 5 | U16 | H'03' | -
Ground i²t setting storage 3: 5 following registers, same as Ground i²t setting storage 1 | - | - | 6465 | 1941 | 5 | U16 | H'03' | -
Ground i²t setting storage 4: 5 following registers, same as Ground i²t setting storage 1 | - | - | 6470 | 1946 | 5 | U16 | H'03' | -
Ground i²t setting storage 5: 5 following registers, same as Ground i²t setting storage 1 | - | - | 6475 | 194B | 5 | U16 | H'03' | -
Neutral protection status setting storage 1: Previous neutral protection status | - | - | 6480 | 1950 | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Neutral protection status setting storage 1: Timestamp machine | s | 1 | 6481 | 1951 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Neutral protection status setting storage 1: Timestamp user | s | 1 | 6483 | 1953 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Neutral protection status setting storage 2: 5 following registers, same as Neutral protection status setting storage 1 | - | - | 6485 | 1955 | 5 | U16 | H'03' | -
Neutral protection status setting storage 3: 5 following registers, same as Neutral protection status setting storage 1 | - | - | 6490 | 195A | 5 | U16 | H'03' | -
Neutral protection status setting storage 4: 5 following registers, same as Neutral protection status setting storage 1 | - | - | 6495 | 195F | 5 | U16 | H'03' | -
Neutral protection status setting storage 5: 5 following registers, same as Neutral protection status setting storage 1 | - | - | 6500 | 1964 | 5 | U16 | H'03' | -
IN setting storage 1: Previous IN setting | % | - | 6505 | 1969 | 1 | U16 | H'03' | Hex 00 00 = 50%, Hex 00 01 = 100%
IN setting storage 1: Timestamp machine | s | 1 | 6506 | 196A | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
IN setting storage 1: Timestamp user | s | 1 | 6508 | 196C | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
IN setting storage 2: 5 following registers, same as IN setting storage 1 | - | - | 6510 | 196E | 5 | U16 | H'03' | -
IN setting storage 3: 5 following registers, same as IN setting storage 1 | - | - | 6515 | 1973 | 5 | U16 | H'03' | -
IN setting storage 4: 5 following registers, same as IN setting storage 1 | - | - | 6520 | 1978 | 5 | U16 | H'03' | -
IN setting storage 5: 5 following registers, same as IN setting storage 1 | - | - | 6525 | 197D | 5 | U16 | H'03' | -
Short time ZSI protection status setting storage 1: Previous Short time ZSI protection status | - | - | 6530 | 1982 | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Short time ZSI protection status setting storage 1: Timestamp machine | s | 1 | 6531 | 1983 | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Short time ZSI protection status setting storage 1: Timestamp user | s | 1 | 6533 | 1985 | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Short time ZSI protection status setting storage 2: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6535 | 1987 | 5 | U16 | H'03' | -
Short time ZSI protection status setting storage 3: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6540 | 198C | 5 | U16 | H'03' | -
Short time ZSI protection status setting storage 4: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6545 | 1991 | 5 | U16 | H'03' | -
Short time ZSI protection status setting storage 5: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6550 | 1996 | 5 | U16 | H'03' | -
Ground fault ZSI protection status setting storage 1: Previous Ground fault ZSI protection status | - | - | 6555 | 199B | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Ground fault ZSI protection status setting storage 1: Timestamp machine | s | 1 | 6556 | 199C | 2 | U32 | H'03' | Example: 35991s: Hex 00 00 8C 97
Ground fault ZSI protection status setting storage 1: Timestamp user | s | 1 | 6558 | 199E | 2 | U32 | H'03' | Example: 34491s: Hex 00 00 86 BB
Ground fault ZSI protection status setting storage 2: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6560 | 19A0 | 5 | U16 | H'03' | -
Ground fault ZSI protection status setting storage 3: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6565 | 19A5 | 5 | U16 | H'03' | -
Ground fault ZSI protection status setting storage 4: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6570 | 19AA | 5 | U16 | H'03' | -
Ground fault ZSI protection status setting storage 5: 5 following registers, same as Short time ZSI protection status setting storage 1 | - | - | 6575 | 19AF | 5 | U16 | H'03' | -

## Configuration
Configuration
Product reference | [7 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | Further information
User Date & time | s | 1 | 6912 | 1B00 | 2 | U32 | H'03' | Example: 34915975s: Hex 02 14 C6 87
System phase sequence | - | - | 6914 | 1B02 | 1 | U16 | H'03' | Hex 00 00=1,2,3; Hex 00 01=1,3,2
Topology | - | - | 6915 | 1B03 | 1 | U16 | H'03' | Hex 00 01=3f3W; Hex 00 02=3f4W
Power sign convention | - | - | 6916 | 1B04 | 1 | U16 | H'03' | Hex 00 00='+'; Hex 00 01='-'
Calculation rule for reactive and apparent power | - | - | 6917 | 1B05 | 1 | U16 | H'03' | Hex 00 00=arithmetic; Hex 00 01=vector
Power factor sign convention | - | 1 | 6918 | 1B06 | 1 | U16 | H'03' | Hex 00 00=IEEE ; Hex 00 01=IEC
Interval duration for On demand values | Min | 1 | 6919 | 1B07 | 1 | U16 | H'03' | Example: 15min: Hex 00 0F
Integration type for On demand values | - | - | 6920 | 1B08 | 1 | U16 | H'03' | Hex 00 00 = fixed, Hex 00 01 = sliding, Hex 00 02 = bus synchronisation
Custom alarm 1: ID alarm | - | - | 6922 | 1B0A | 1 | U16 | H'03' | Example: Custom alarm ID 39: Hex 00 27
Custom alarm 1: Alarm priority | - | - | 6923 | 1B0B | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Custom alarm 1: Pick-up threshold | - | - | 6924 | 1B0C | 1 | U16 | H'03' | Example: Custom alarm ID 39, Over unbalanced voltage value U12, resolution 0,1%: over 5%: Hex 00 32
Custom alarm 1: Pick-up time delay | s | - | 6925 | 1B0D | 1 | U16 | H'03' | Example: 35991s: Hex 00 00 8C 97
Custom alarm 1: Drop-out threshold | - | - | 6926 | 1B0E | 1 | U16 | H'03' | Example: Custom alarm ID 39, Over unbalanced voltage value U12, resolution 0,1%: Drop-out 4%: Hex 00 28
Custom alarm 1: Drop-out time delay | s | - | 6927 | 1B0F | 1 | U16 | H'03' | Example: 34491s: Hex 00 00 86 BB
Custom alarm 2: 6 following registers, same as Custom alarm 1 |  | - | 6928 | 1B10 | 6 | U16 | H'03' | -
Custom alarm 3: 6 following registers, same as Custom alarm 1 |  | - | 6934 | 1B16 | 6 | U16 | H'03' | -
Custom alarm 4: 6 following registers, same as Custom alarm 1 |  | - | 6940 | 1B1C | 6 | U16 | H'03' | -
Custom alarm 5: 6 following registers, same as Custom alarm 1 |  | - | 6946 | 1B22 | 6 | U16 | H'03' | -
Custom alarm 6: 6 following registers, same as Custom alarm 1 |  | - | 6952 | 1B28 | 6 | U16 | H'03' | -
Custom alarm 7: 6 following registers, same as Custom alarm 1 |  | - | 6958 | 1B2E | 6 | U16 | H'03' | -
Custom alarm 8: 6 following registers, same as Custom alarm 1 |  | - | 6964 | 1B34 | 6 | U16 | H'03' | -
Custom alarm 9: 6 following registers, same as Custom alarm 1 |  | - | 6970 | 1B3A | 6 | U16 | H'03' | -
Custom alarm 10: 6 following registers, same as Custom alarm 1 |  | - | 6976 | 1B40 | 6 | U16 | H'03' | -
Custom alarm 11: 6 following registers, same as Custom alarm 1 |  | - | 6982 | 1B46 | 6 | U16 | H'03' | -
Custom alarm 12: 6 following registers, same as Custom alarm 1 |  | - | 6988 | 1B4C | 6 | U16 | H'03' | -
Long time trip Alarm priority |  | - | 6994 | 1B52 | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Short time trip Alarm priority |  | - | 6995 | 1B53 | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Instantaneous trip Alarm priority |  | - | 6996 | 1B54 | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Ground fault trip Alarm priority |  | - | 6997 | 1B55 | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Test trip Alarm priority |  | - | 6998 | 1B56 | 1 | U16 | H'03' | Hex 00 00 = no priority, Hex 00 01 = low priority, Hex 00 02 = medium priority, Hex 00 03 = high priority
Overload prealarm PTA Pick-up threshold | % | 5 | 6999 | 1B57 | 1 | U16 | H'03' | Example: 90% x Ir: Hex 00 5A
Overload prealarm PTA Pick-up time delay | % | 5 | 7000 | 1B58 | 1 | U16 | H'03' | Example: 50% x tr: Hex 00 32
Overload prealarm PTA enable | - | 1 | 7001 | 1B59 | 1 | U16 | H'03' | Hex 00 00 = alarm disable, Hex 00 01 = alarm enable
OAC output contact behaviour | - | - | 7002 | 1B5A | 1 | U16 | H'03' | Hex 00 00 = auto reset, Hex 00 01 = latching
OAC output contact alarm assignment ID | - | - | 7003 | 1B5B | 1 | U16 | H'03' | Example: Assignment ID 4: Overload prealarm: Hex 00 04
Ir threshold | A | 1 | 7005 | 1B5D | 1 | U16 | H'03' | Example: Ir 63A: Hex 00 3F
tr time delay | s | 0.25 | 7006 | 1B5E | 1 | U16 | H'03' | Example: tr 2,5s: Hex 00 0A
Short time protection status | - | - | 7007 | 1B5F | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Isd threshold | x Ir | 0.5 | 7008 | 1B60 | 1 | U16 | H'03' | Example: 5 x Ir: Hex 00 0A
tsd time delay | ms | - | 7009 | 1B61 | 1 | U16 | H'03' | Example: 200ms: Hex 00 C8
Short i²t setting status | - | - | 7010 | 1B62 | 1 | U16 | H'03' | Hex 00 00 = I²t disable, Hex 00 01 = I²t enable
Short time ZSI protection status | - | - | 5445 | 1B63 | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Instantaneous protection status | - | - | 7012 | 1B64 | 1 | U16 | H'03' | Read only data. Hex 00 00 = protection disable, Hex 00 01 = protection enable
Ii threshold | x In | 0.5 | 7013 | 1B65 | 1 | U16 | H'03' | Example: 10 x In: Hex 00 14
Ground fault protection status | - | - | 7014 | 1B66 | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Ig threshold | x In | 0.05 | 7015 | 1B67 | 1 | U16 | H'03' | Example: 0.2 x In: Hex 00 04
tg time delay | ms | - | 7016 | 1B68 | 1 | U16 | H'03' | Example: 200ms: Hex 00 C8
Ground i²t setting status | - | - | 7017 | 1B69 | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Ground fault ZSI protection status | - | - | 7018 | 1B6A | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Neutral protection status | - | - | 7019 | 1B6B | 1 | U16 | H'03' | Hex 00 00 = protection disable, Hex 00 01 = protection enable
Neutral threshold | - | - | 7020 | 1B6C | 1 | U16 | H'03' | Hex 00 00 = 50%, Hex 00 01 = 100%
Data writing autorisation status | - | - | 7021 | 1B6D | 1 | U16 | H'03' | Read only data. 0 = bus write access allowed, 1 = bus write access not allowed
Custom field 1 (up to 32 characters) | - | 1 | 7022 | 1B6E | 16 | STRING | H'03' | ASCII code
Custom field 2 (up to 32 characters) | - | 1 | 7038 | 1B7E | 16 | STRING | H'03' | ASCII code

## Communication
Communication
Product reference | [7 empty] | HTC310H, HTC320H + HHSxxxNx, HNSxxxNx, HMSxxxNx, HESxxxNx HHTxxxNR, HNTxxxNR, HMTxxxNR, HETxxxNR
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | Further information
MCCB COM bus status | - | - | 8192 | 2000 | 1 | U16 | H'03' | Hex 00 00 = Not connected, Hex 00 01 = Initializing, Hex 00 02 = Operating normal, Hex 00 03 = Operating optimized
MCCB COM bus request counter | - | 1 | 8194 | 2002 | 2 | U32 | H'03' | Example: 2: Hex 00 00 00 02
MCCB COM bus down | s | 1 | 8196 | 2004 | 2 | U32 | H'03' | Example: 75s: Hex 00 00 00 4B
MCCB COM bus communication error number | - | 1 | 8198 | 2006 | 2 | U32 | H'03' | Example:1149: Hex 00 00 04 7D
MODBUS communication error number | - | 1 | 8200 | 2008 | 2 | U32 | H'03' | Example:1149: Hex 00 00 04 7D
Output 1 Counter | - | 1 | 8202 | 200A | 1 | U16 | H'03' | Only HTC320H Example: 2: Hex 00 02
Output 2 Counter | - | 1 | 8203 | 200B | 1 | U16 | H'03' | Only HTC320H Example: 2: Hex 00 02
Running duration counter | h | 1 | 8204 | 200C | 2 | U32 | H'03' | Example: 8544h: Hex 00 00 21 60
Modbus configuration address | - | 1 | 8221 | 201D | 1 | U16 | H'03' | Example: 1: Hex 00 01
Modbus configuration baudrate | - | 1 | 8222 | 201E | 2 | U32 | H'03' | Example: 19200: Hex 00 00 4B 00
Modbus configuration stop bits | - | 1 | 6922 | 1B0A | 1 | U16 | H'03' | Example: 1: Hex 00 01
Modbus configuration parity | - | 1 | 6923 | 1B0B | 1 | U16 | H'03' | Example: Odd: Hex 00 01
Modbus configuration Line termination resistor | - | - | 8230 | 2026 | 1 | U16 | H'03' | Hex 00 00=resistor not activated; Hex 00 01=resistor activated
Digital input 1 |  | 1 | 8232 | 2028 | 1 | U16 | H'03' | Only HTC320H Hex 00 00=Opened; Hex 00 01=Closed
Digital input 2 |  | 1 | 8233 | 2029 | 1 | U16 | H'03' | Only HTC320H Hex 00 00=Opened; Hex 00 01=Closed
MCCB Refresh time | ms | 1 | 8235 | 202B | 1 | U16 | H'03' | Example: 1789ms: Hex 06 FD
Pulse mode output 1 |  | 1 | 8320 | 2080 | 1 | U16 | H'03', H'06', H'16' | Only HTC320H Hex 00 00 = binary mode, Hex 00 01 = configurable pulse mode
Pulse mode output 2 |  | 1 | 8321 | 2081 | 1 | U16 | H'03', H'06', H'16' | Only HTC320H Hex 00 00 = binary mode, Hex 00 01 = configurable pulse mode
Output 1 write |  | 1 | 8322 | 2082 | 1 | U16 | H'03', H'06', H'16' | if pulse mode = Hex 00 00, then Hex 00 00 = Close, Hex 00 01 = Open. if pulse mode = Hex 00 01, then send pulse command with duration in ms; Example 300ms: Hex 01 2C.
Output 2 write |  | 1 | 8323 | 2083 | 1 | U16 | H'03', H'06', H'16' | if pulse mode = Hex 00 00, then Hex 00 00 = Close, Hex 00 01 = Open. if pulse mode = Hex 00 01, then pulse duration in ms; Example 300ms: Hex 01 2C.
Credential level |  | 1 | 8706 | 2202 | 1 | U16 | H'03', H'16' | -
Length of password |  | 1 | 8707 | 2203 | 1 | U16 | H'03', H'16' | -
Modbus Password |  | 1 | 8708 | 2204 | 4 | STRING | H'03', H'16' | -
Token response status |  | 1 | 8712 | 2208 | 1 | U16 | H'03' | -
Token value |  | 1 | 8713 | 2209 | 2 | U32 | H'03' | -
Command response status |  | 1 | 8736 | 2220 | 1 | U16 | H'03' | -
Token value |  | 1 | 8737 | 2221 | 2 | U32 | H'03', H'16' | -
Command ID |  | 1 | 8739 | 2223 | 1 | U16 | H'03', H'16' | -
Parameters length |  | 1 | 8740 | 2224 | 1 | U16 | H'03', H'16' | -
Parameters data |  | 1 | 8741 | 2225 | 16 | U16 | H'03', H'16' | -